## README
Adlar Aurora III — Modbus Register Map (verzameld)
Startpunt voor het destilleren van een definitieve register map
Bijgewerkt naar app-versie 1.9.3 (oktober 2026): zie tabblad 'Status app 1.9.3' en de kolom 'Status app 1.9.3' per tabblad. De oorspronkelijke analyse hieronder is ongewijzigd behouden.
Bron 1 — Spec: 'Adlar-III_modbus_registers_HHi.xlsx', tabblad 'Register Map' (leidend, 125 registers)
Bron 2 — Implementatie: 'adlar_heatpump.yaml' (Home Assistant configuratie, gebruikt 12 registers)
Bron — Uitgebreide HA-package 'adlar_warmtepomp.yaml' (2026) en de Homey-app (lib/modbus/adlar3-modbus-registers.ts). Bij tegenspraak is de officiële register map leidend.
Tabbladen in dit document:
1. Register Map (master) — alle 125 registers uit de spec, verrijkt met implementatie-info en discrepantie-flags
2. HA Integration — afgeleide entiteiten (templates, binary_sensors, climate, select, counters)
3. Discrepancies & Notes — typo's, ontbrekende scale-factoren, bit-encoding gaten
4. Coverage & Roadmap — wat is in gebruik, wat is bruikbaar maar niet ontsloten, prioriteit per uitbreiding
Kleurcodering Register Map (master):
Groen = register is in YAML gebruikt
Geel = writable register (Read/Write) — schrijfacties richting de pomp
Oranje = scale/encoding open punt (zie Discrepancies)
Compatibiliteitsanalyse spec ↔ YAML:
• Geen scale-conflicten op de 12 actieve registers
• 12/125 (≈10%) van de registers operationeel ontsloten
• 3/15 schrijfbare registers in gebruik (2100, 2103, 2107)
• Conclusie: merge is realiseerbaar; spec en YAML zijn consistent waar ze overlappen
Aanbevolen vervolgstappen:
1. Verifieer 4 verdachte 'x1' scale-waardes op °C-registers (zie Discrepancies, vooral Reg 2109 — schrijfbaar!)
2. Reverse-engineer de bit-mapping van Reg 38 (system status) en Reg 2103 (additional function A) volledig
3. Log Reg 102/103 tijdens bedrijf om operation-mode enums vast te stellen
4. Overweeg ontsluiting van DHW (Reg 46, 2102, 2105), zone 2 (Reg 47, 2110-2113) en P/T-bewaking (Reg 86, 87)

## Status app 1.9.3
Register | Officiële register map | App 1.9.3 | Capability / functie | Afwijking / opmerking | Hardwareverificatie
3-1 | 0 = geen thermostaat; 1-3 = met thermostaat (enkele zone / twee zones) | Gelezen bij verbinden | — | 4-2114 werkt mogelijk niet zonder thermostaat | —
3-2 | 0 = één zone, 1 = twee zones | Gelezen bij verbinden | Standaardwaarde bij aanzetten via 4-2101 (1 of 3) | — | —
3-7 | Koudemiddel: 0 = R32, 1 = R290 | Gelezen bij verbinden | Bepaalt of stille modus niveau 2 is toegestaan | Map: niveau 2 alleen voor R290 | —
3-9 | Effectieve modus: bit 0 koelen, bit 1 verwarmen, bit 2 tapwater | Medium-poll (30 s) | adlar_dhw_active; gebouwmodel slaat tapwaterperiodes over | — | —
3-10..31 | Statische limieten per zone en modus | Slow-poll (5 min) | 3-14/15 begrenzen 4-2105; 3-30/31 begrenzen 4-2114 | Map-typo x1 bij 3-16 en 3-27 | Schaal 3-16/27
3-38 | Systeemstatus (bitveld) | Superfast-poll | adlar_defrosting, adlar_antifreeze, adlar_sterilization | Bits 0, 1, 2, 4, 11 bekend (HA) | Overige bits
3-39 | B0/B1: aanvraag externe warmtebron tijdens vorstbeveiliging / ontdooien (alleen hybride) | Gelezen, niet gedecodeerd; bittabel in expertdashboard | — | HA-YAML noemt het externe vorstbeveiliging/ontdooien; app volgt de map (gecorrigeerd in 1.9.3) | —
3-63 | Titel: PWM-percentage terugkoppeling; schaal x10, eenheid m³/h | x0.1 m³/h, alleen dashboard | — | Map spreekt zichzelf tegen; HA leest % x1. App volgt de map (gecorrigeerd in 1.9.3) | Ja
3-64 | Werkelijk debiet, m³/h, schaal niet opgegeven | x0.1 m³/h, getoond in L/min | measure_water | — | Eenheid/schaal
3-66..69 | Stooklijn-setpoints | Slow-poll (was eenmalig) | Dashboard | — | —
3-67 | Schaal x1 | x0.1 (zoals HA), @verify | Dashboard | Map x1 tegenover HA x10 | Ja
3-74/75 | Spanning x1 V, stroom x10 A | Spanning × stroom = vermogen | measure_power, measure_voltage, measure_current | Geven op sommige firmware 0 (HA); app logt dit eenmalig | Non-lineariteit stroomsensor
3-81 | Vierwegklep: 0 uit, 1 aan | Gelezen | Dashboard | HA: 1 = koelen/ontdooien | —
3-90..95 | E01-E96, bit voor bit | Bitveld → E-codes (bijv. E03) | adlar_fault, adlar_fault_active, alarm_generic, flowtrigger fault_detected | Tot 1.9.0: één code per register | Omschrijving per code
3-96..101 | P01-P96, bit voor bit (3-101 = P81-P96) | Bitveld → P-codes | Idem | HA-YAML leest 3-101 als doelmodus; volgens de map onjuist | —
3-102 | Doelmodus: B3-B0 zone 1, B7-B4 zone 2 (0 standby, 1 koelen, 2 verwarmen), B11-B8 tapwater (0 standby, 8 tapwater) | Gelezen, niet gedecodeerd | Dashboard | Bovenste bits (auto-doelmodus) onduidelijk in de map | —
3-103 | Werkelijke modus: zelfde indeling als 3-102 | Gelezen, niet gedecodeerd | Dashboard | — | —
4-2100 | 1 koelen, 2 verwarmen, 4 auto | Lezen en schrijven (1/2/4) | adlar_mode | 0 wordt nooit geschreven; aan/uit via 4-2101 | —
4-2101 | 0 alles uit, 1 zone 1 aan, 2 zone 2 aan, 3 alles aan | Lezen; schrijven alleen met instelling 'Aan/uit via zonebesturing (experimenteel)' | onoff | — | Ja (testgebruikers)
4-2102 | 0 tapwater uit, 1 aan | Lezen en schrijven | adlar_dhw_enabled, flowkaart set_dhw_function | — | —
4-2103 bit 3 | Geforceerde elektrische verwarming | Read-modify-write | adlar_backup_heater_forced, flowkaart set_backup_heater | — | Ja (overige bits behouden)
4-2103 bit 4-5 | Stille modus 0/1/2; niveau 2 alleen R290 | Read-modify-write; niveau 2 alleen bij 3-7 = R290 (1.9.3) | adlar_silent_mode, flowkaarten set_silent_mode / silent_mode_is | — | Ja
4-2103 bit 6 | Desinfectiemodus (schrijfbaar) | Alleen lezen | adlar_disinfection_enabled | Bewust niet schrijfbaar gemaakt | —
4-2105 | Tapwater-setpoint x10 | Lezen en schrijven, begrensd door 3-14/15 | target_temperature.dhw | — | —
4-2107 | Zone 1 verwarmings-setpoint x10 | Lezen en schrijven | target_temperature | Wordt overschreven door de eigen stooklijn van de regelaar (JAN-module) | —
4-2109 | Zone 1 auto-verwarming, schaal x1 volgens map | Schrijven geblokkeerd | — | Vermoedelijk typo (x10) | Ja
4-2114 | Kamertemperatuur-setpoint x10 | Lezen; schrijven via dashboard (16-28 °C of 3-31..30) | target_temperature.floor (weergave) | — | Werking zonder thermostaat

## Register Map (master)
Modbus Register | Hex Address | Data Type | Access | Data Content | Description | Scale Factor | Unit | In YAML? | HA Entity Name | HA Input Type | HA Scale | Scan Interval (s) | Implementation Notes | Has Discrepancy? | In app 1.9.3? | App 1.9.3 — gebruik
0 | 0X0000 | U16 | Read Only | Total number of addresses | Since 3X0000 (including 3X0000)
1 | 0X0001 | U16 | Read Only | Third party thermostat controller type | 0: without third party thermostat 1: with third party thermostat(single zone control: on/off and mode change) 2: with third party thermostat(single zone control: on/off) 3: with third party thermostat(two zones control: on/off) | [9 empty] | Yes | Gelezen bij verbinden
2 | 0X0002 | U16 | Read Only | Without third party thermostat single zone or two zones control | 0: 1: 0: single zone, 1: two zones | [9 empty] | Yes | Standaard zone-waarde voor aan/uit
3 | 0X0003 | U16 | Read Only | Without third party thermostat for single zone control | 0: the setting water temperature works as the target temperature to turn on/off the unit 1: the climate curves setting water temperature works as the target temperature to turn on/off the unit 2 reserved: the setting water temperature works as the target temperature and room setting temperature is used to turn on/off the unit 3: the climate curves setting water temperature works as the target temperature and room setting temperature works to turn on/off the unit
4 | 0X0004 | U16 | Read Only | Without third party thermostat for two zones control | Complex multi-zone control modes (0-7)
5 | 0X0005 | U16 | Read Only | With thermostat single zone control | 0: the manual setting water temperature works as the target temperature to turn on/off the unit 1: the climate curves setting water temperature works as the target temperature to turn on/off the unit
6 | 0X0006 | U16 | Read Only | With thermostat two zones control | 0: both zone 1/2: the setting water temperature works as the target temperature to turn on/off the unit 1: zone 1: the manual setting water temperature... 2: zone 1: climate curves setting water temperature... 3: both zone 1/2: the climate curves setting water temperature works as the target temperature to turn on/off the unit
7 | 0X0007 | U16 | Read Only | Refrigerant type | 0: R32 R32 Series 1: R290 R290 Series | [9 empty] | Yes | Bepaalt stille modus niveau 2 (R290)
8 | 0X0008 | U16 | Read Only | Unit type | Bit[5:1] Bit[0](1)
9 | 0X0009 | U16 | Read Only | Effective mode | Bit[15:3]: Reserved Bit[2](1): DHW mode effective or not(1 means effective) Bit[1](1): Heating mode effective or not(1 means effective) Bit[0](1): Cooling mode effective or not(1 means effective) | [8 empty] | Yes | Yes | adlar_dhw_active
10 | 0X0010 | S16 | Read Only | Zone 1 cooling mode temperature setting upper limit |  | x10 | °C
11 | 0X0011 | S16 | Read Only | Zone 1 cooling mode temperature setting lower limit |  | x10 | °C
12 | 0X0012 | S16 | Read Only | Zone 1 heating mode temperature setting upper limit |  | x10 | °C
13 | 0X0013 | S16 | Read Only | Zone 1 heating mode temperature setting lower limit |  | x10 | °C
14 | 0X0014 | S16 | Read Only | Zone 1 DHW mode temperature setting upper limit |  | x10 | °C | [7 empty] | Yes | Bovengrens 4-2105
15 | 0X0015 | S16 | Read Only | Zone 1 DHW mode temperature setting lower limit |  | x10 | °C | [7 empty] | Yes | Ondergrens 4-2105
16 | 0X0016 | S16 | Read Only | Zone 1 auto cooling temperature setting upper limit | For example: 123 means 123 degree celsius | x1 | °C | [6 empty] | Yes
17 | 0X0017 | S16 | Read Only | Zone 1 auto cooling temperature setting lower limit |  | x10 | °C
18 | 0X0018 | S16 | Read Only | Zone 1 auto heating temperature setting upper limit |  | x10 | °C
19 | 0X0019 | S16 | Read Only | Zone 1 auto heating temperature setting lower limit |  | x10 | °C
20 | 0X0020 | S16 | Read Only | Zone 2 cooling mode temperature setting upper limit |  | x10 | °C
21 | 0X0021 | S16 | Read Only | Zone 2 cooling mode temperature setting lower limit |  | x10 | °C
22 | 0X0022 | S16 | Read Only | Zone 2 heating mode temperature setting upper limit |  | x10 | °C
23 | 0X0023 | S16 | Read Only | Zone 2 heating mode temperature setting lower limit |  | x10 | °C
24 | 0X0024 | U16 | Read Only | Reserved
25 | 0X0025 | U16 | Read Only | Reserved
26 | 0X0026 | S16 | Read Only | Zone 2 auto mode cooling temperature setting upper limit |  | x10 | °C
27 | 0X0027 | S16 | Read Only | Zone 2 auto mode cooling temperature setting lower limit | For example: 123 means 123 degree celsius | x1 | °C | [6 empty] | Yes
28 | 0X0028 | S16 | Read Only | Zone 2 auto mode heating temperature setting upper limit |  | x10 | °C
29 | 0X0029 | S16 | Read Only | Zone 2 auto mode heating temperature setting lower limit |  | x10 | °C
30 | 0X0030 | S16 | Read Only | Room temperature setting upper limit | For example: 123 means 12.3 degree celsius | x10 | °C | [7 empty] | Yes | Bovengrens 4-2114
31 | 0X0031 | S16 | Read Only | Room temperature setting lower limit |  | x10 | °C | [7 empty] | Yes | Ondergrens 4-2114
32 | 0X0032 | U16 | Read Only | Reserved
33 | 0X0033 | U16 | Read Only | Reserved
34 | 0X0034 | U16 | Read Only | Zone 1 terminal type for cooling
35 | 0X0035 | U16 | Read Only | Zone 1 terminal type for heating | 0: FCU, 1: Radiator, 2: Floor heating circuit
36 | 0X0036 | U16 | Read Only | Zone 2 terminal type for cooling
37 | 0X0037 | U16 | Read Only | Zone 2 terminal type for heating
38 | 0X0038 | U16 | Read Only | System status | B15-B12: Reserved B11: Ambient temp. too low, compressor can not be started B10-B8: Reserved B7-B5: Reserved B4: Disinfection mode is running B3: Reserved B2: Anti-freezing mode is running B1: Defrosting mode is running B0: Oil return mode is running 0: off, 1: on |  |  | Yes | WP System status bits | input | 1 | 30 | Bitmask: bit0=oil return, bit1=defrost, bit2=anti-freeze, bit4=desinfectie, bit11=low-temp block | Yes | Yes | adlar_defrosting, adlar_antifreeze, adlar_sterilization
39 | 0X0039 | U16 | Read Only | Request external heating source (only for hybrid solution) | B15-B4: Reserved B3: Reserved B2: Reserved B1: Request external heating source during defrosting mode B0: Request external heating source during anti-freezing mode 0: off, 1: on | [9 empty] | Yes | Gelezen (bittabel dashboard)
40 | 0X0040 | S16 | Read Only | Room temperature Tldr |  | x10 | °C | [7 empty] | Yes | Dashboard
41 | 0X0041 | S16 | Read Only | Total leaving water temperature TC (after auxiliary gas boiler heaters) |  | x10 | °C | [7 empty] | Yes | measure_temperature.total_outlet
42 | 0X0042 | S16 | Read Only | Inlet water temperature TA |  | x10 | °C | Yes | WP Retour temperatuur | input | 0.1 | 30 | Gebruikt in DeltaT template-sensor |  | Yes | measure_temperature.inlet
43 | 0X0043 | S16 | Read Only | Leaving water temperature TE1 |  | x10 | °C | Yes | WP Aanvoer temperatuur | input | 0.1 | 30 | Climate entity 'Warmtepomp' leest huidige temp van dit register |  | Yes | measure_temperature.outlet
44 | 0X0044 | S16 | Read Only | Buffer tank upper part temperature TE2 (reserved) |  | x10 | °C
45 | 0X0045 | S16 | Read Only | Buffer tank lower part temperature TW |  | x10 | °C | [7 empty] | Yes | measure_temperature.buffer_tank
46 | 0X0046 | S16 | Read Only | DHW water tank temperature TZ2 | For example: 123 means 12.3 degree celsius | x10 | °C | [7 empty] | Yes | measure_temperature.dhw
47 | 0X0047 | S16 | Read Only | Zone 2 mixing station inlet water temperature Tso |  | x10 | °C | [7 empty] | Yes | measure_temperature.zone2
48 | 0X0048 | S16 | Read Only | Solar water heating temperature T3 |  | x10 | °C | [6 empty] | Yes
49 | 0X0049 | S16 | Read Only | Outdoor unit coil temperature T3 |  | x10 | °C | [6 empty] | Yes | Yes | measure_temperature.outer_coil
50 | 0X0050 | S16 | Read Only | Ambient temperature T4 |  | x10 | °C | Yes | WP Buiten temperatuur | input | 0.1 | 30 |  |  | Yes | measure_temperature.ambient
51 | 0X0051 | S16 | Read Only | Outlet temperature of the EXV valve T5 |  | x10 | °C
52 | 0X0052 | S16 | Read Only | Discharge temperature TP |  | x10 | °C | [7 empty] | Yes | measure_temperature.exhaust
53 | 0X0053 | S16 | Read Only | Suction temperature TH |  | x10 | °C | [7 empty] | Yes | measure_temperature.suction
54 | 0X0054 | S16 | Read Only | Reserved
55 | 0X0055 | S16 | Read Only | Reserved
56 | 0X0056 | S16 | Read Only | Target outlet setting temperature TOut |  | x10 | °C | [7 empty] | Yes | Dashboard
57 | 0X0057 | U16 | Read Only | Reserved
58 | 0X0058 | U16 | Read Only | Reserved
59 | 0X0059 | U16 | Read Only | Reserved
60 | 0X0060 | U16 | Read Only | Inlet water pressure (reserved) | For example: 123 means 12.3Bar | x10 | Bar | [7 empty] | Yes | Dashboard
61 | 0X0061 | U16 | Read Only | Outlet water pressure |  |  | Bar | Yes | WP Outlet water pressure | input | 0.1 | 30 |  | Yes | Yes | Dashboard
62 | 0X0062 | U16 | Read Only | PWM - Percentage of output PWM of DC water pump | For example: 123 means 123% | x1 | % | Yes | WP Percentage PWM output | input | 1 | 30 | YAML scale=1, spec scale=x1 → consistent |  | Yes | adlar_pump_pwm
63 | 0X0063 | U16 | Read Only | PWM - Percentage of feedback PWM of DC water pump | For example: 123 means 12.3m3/h | x10 | m³/h | [7 empty] | Yes | Dashboard (x0.1 m³/h, @verify)
64 | 0X0064 | U16 | Read Only | Actual water flow of the DC pump |  |  | m³/h | Yes | WP Water flow | input | 0.1 | 30 | Gebruikt in Thermisch vermogen template-sensor | Yes | Yes | measure_water
65 | 0X0065 | U16 | Read Only | Reserved
66 | 0X0066 | S16 | Read Only | Zone 1 climate curve cooling set temperature |  | x10 | °C | [7 empty] | Yes | Dashboard
67 | 0X0067 | S16 | Read Only | Zone 1 climate curve heating set temperature | For example: 123 means 123 degree celsius | x1 | °C | [6 empty] | Yes | Yes | Dashboard (x0.1, @verify)
68 | 0X0068 | S16 | Read Only | Zone 2 climate curve cooling set temperature |  | x10 | °C | [7 empty] | Yes | Dashboard
69 | 0X0069 | S16 | Read Only | Zone 2 climate curve heating set temperature |  | x10 | °C | [7 empty] | Yes | Dashboard
70 | 0X0070 | U16 | Read Only | EEV Main EEV open degree | For example: 123 means 123 steps | x1 | steps | [7 empty] | Yes | adlar_eev_step
71 | 0X0071 | U16 | Read Only | EEV Auxiliary EEV open degree Reserved | [10 empty] | Yes | adlar_evi_step
72 | 0X0072 | U16 | Read Only | 1 Speed of No.1 DC fan | For example: 123 means 123 Revolutions per minute | x1 | RPM | Yes | WP fan speed | input | 1 | 30 |  |  | Yes | adlar_fan_speed
73 | 0X0073 | U16 | Read Only | 2 Reserved
74 | 0X0074 | U16 | Read Only | AC input voltage | For example: 123 means 123V | x1 | V | [7 empty] | Yes | measure_voltage, measure_power
75 | 0X0075 | U16 | Read Only | AC input current | For example: 123 means 12.3A | x10 | A | [7 empty] | Yes | measure_current, measure_power
76 | 0X0076 | U16 | Read Only | DC bus voltage | For example: 123 means 123V | x1 | V | [7 empty] | Yes | Dashboard
77 | 0X0077 | U16 | Read Only | Compressor current | For example: 123 means 12.3A | x10 | A | [7 empty] | Yes | measure_current.comp_phase
78 | 0X0078 | U16 | Read Only | Compressor target frequency |  |  | Hz | [7 empty] | Yes | measure_frequency.comp_target_freq
79 | 0X0079 | U16 | Read Only | Compressor actual frequency | For example: 123 means 123Hz | x1 | Hz | Yes | WP Compressor frequentie | input | 1 | 30 |  |  | Yes | measure_frequency.compressor_freq, adlar_compressor_on
80 | 0X0080 | U16 | Read Only | Main water pump on/off status (unit internal circulation water pump) | 0: off, 1: on | [9 empty] | Yes | adlar_running
81 | 0X0081 | U16 | Read Only | Four way valve on/off status | 0: off, 1: on | [9 empty] | Yes | Dashboard
82 | 0X0082 | U16 | Read Only | Reserved
83 | 0X0083 | U16 | Read Only | Reserved
84 | 0X0084 | U16 | Read Only | Reserved
85 | 0X0085 | U16 | Read Only | Reserved
86 | 0X0086 | U16 | Read Only | High pressure |  |  | kPa | [6 empty] | Yes | Yes | adlar_high_pressure
87 | 0X0087 | U16 | Read Only | Low pressure | For example: 123 means 123kpa | x1 | kPa | [7 empty] | Yes | adlar_low_pressure
88 | 0X0088 | U16 | Read Only | Reserved
89 | 0X0089 | U16 | Read Only | Reserved
90 | 0X0090 | U16 | Read Only | E01-E16 | E01-E96 bit by bit operation 3X0090 bit0 1E01 For example, if the bit0 of 3X0090 is 1, E01 is the error code 3X0091 bit1 1E18 For example, if the bit1 of 3X0091 is 1, E18 is the error code | [9 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
91 | 0X0091 | U16 | Read Only | E17-E32 | [10 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
92 | 0X0092 | U16 | Read Only | E33-E48 | [10 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
93 | 0X0093 | U16 | Read Only | E49-E64 | [10 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
94 | 0X0094 | U16 | Read Only | E65-E80 | [10 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
95 | 0X0095 | U16 | Read Only | E81-E96 | [10 empty] | Yes | Bitveld → E-codes (adlar_fault_active)
96 | 0X0096 | U16 | Read Only | P01-P16 | P01-P96 bit by bit operation 3X0096 bit0 1P01 For example, if the bit0 of 3X0096 is 1, P01 is the error code 3X0097 bit1 1P18 For example, if the bit0 of 3X0097 is 1, P18 is the error code | [9 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
97 | 0X0097 | U16 | Read Only | P17-P32 | [10 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
98 | 0X0098 | U16 | Read Only | P33-P48 | [10 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
99 | 0X0099 | U16 | Read Only | P49-P64 | [10 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
100 | 0X0100 | U16 | Read Only | P65-P80 | [10 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
101 | 0X0101 | U16 | Read Only | P81-P96 | [10 empty] | Yes | Bitveld → P-codes (adlar_fault_active)
102 | 0X0102 | U16 | Read Only | Current target operation mode | B15-B9: Auto target mode 0X01: Cooling mode 0X02: Heating mode 0X11-B8: DHW target mode 0X00: Standby mode 0X08: DHW mode B7-B4: Two zones control: zone 2 air conditioner target mode 0X00: Standby mode 0X01: Cooling mode 0X02: Heating mode B3-B0: Two zones control: zone 1 air conditioner target mode One zone control: air conditioner target mode 0X00: Standby mode 0X01: Cooling mode 0X02: Heating mode |  | A | [6 empty] | Yes | Yes | Dashboard
103 | 0X0103 | U16 | Read Only | Actual operation mode | B15-B9: Reserved B11-B8: DHW operation mode 0X00: Standby 0X08: DHW mode B7-B4: Two zones control: zone 2 air conditioner operation mode 0X00: Standby 0X01: Cooling 0X02: Heating B3-B0: Two zones control: zone 1 air conditioner operation mode One zone control: air conditioner operation mode 0X00: Standby 0X01: Cooling 0X02: Heating | [8 empty] | Yes | Yes | Dashboard
104 | 0X0104 | U16 | Read Only | Reserved
105 | 0X0105 | U16 | Read Only | Reserved
106 | 0X0106 | U16 | Read Only | Reserved
107 | 0X0107 | U16 | Read Only | Reserved
108 | 0X0108 | U16 | Read Only | Reserved
109 | 0X0109 | U16 | Read Only | Reserved
2100 | 0X2100 | U16 | Read/Write | Air condition modes | 1: Cooling mode 2: Heating mode 4: Auto mode |  |  | Yes | Climate HVAC mode register | holding | 1 |  | Mapping: 1=cool, 2=heat, 4=auto |  | Yes | adlar_mode
2101 | 0X2101 | U16 | Read/Write | Air condition modes (zone control) | 0: All off 1: Zone 1 on, zone 2 off 2: Zone 1 off, zone 2 on 3: All on | [9 empty] | Yes | onoff (schrijven experimenteel)
2102 | 0X2102 | U16 | Read/Write | DHW mode on/off | 0: DHW off 1: DHW on | [9 empty] | Yes | adlar_dhw_enabled
2103 | 0X2103 | U16 | Read/Write | Additional function A | Bit[15-8]: Reserved Bit[7]: Reserved Bit[6]: Disinfection mode Bit[5-4]: Silent mode 0: Silent mode off 1: Silent mode level one 2: Silent mode level two (only for R290 heat pumps) Bit[3]: Forced electrical heater Bit[2]: Reserved Bit[1]: Reserved Bit[0]: Reserved 0: off, 1: on |  |  | Yes | WP Silent mode raw | holding | 1 | 30 | Bits 4-5 = silent level (0=uit, 1=niveau1, 2=niveau2). Andere bits behouden via cleared+offset | Yes | Yes | adlar_backup_heater_forced (b3), adlar_silent_mode (b4-5), adlar_disinfection_enabled (b6)
2104 | 0X2104 | U16 | Read/Write | B() Additional function A (Reserved) | 0: off 1: on
2105 | 0X2105 | S16 | Read/Write | DHW mode water temperature setting |  | x10 | °C | [7 empty] | Yes | target_temperature.dhw
2106 | 0X2106 | S16 | Read/Write | Zone 1 cooling mode temperature setting |  | x10 | °C | [7 empty] | Yes | target_temperature.cooling
2107 | 0X2107 | S16 | Read/Write | Zone 1 heating mode temperature setting |  | x10 | °C | Yes | WP Setpoint zone 1 verwarming | holding | 0.1 |  | Schrijfbaar via number platform en climate entity |  | Yes | target_temperature
2108 | 0X2108 | S16 | Read/Write | Zone 1 auto mode cooling temperature setting |  | x10 | °C
2109 | 0X2109 | S16 | Read/Write | Zone 1 auto mode heating temperature setting | For example: 123 means 123 degree celsius | x1 | °C | [6 empty] | Yes | Yes | Schrijven geblokkeerd
2110 | 0X2110 | S16 | Read/Write | Zone 2 cooling mode temperature setting |  | x10 | °C
2111 | 0X2111 | S16 | Read/Write | Zone 2 heating mode temperature setting |  | x10 | °C
2112 | 0X2112 | S16 | Read/Write | Zone 2 auto mode cooling temperature setting |  | x10 | °C
2113 | 0X2113 | S16 | Read/Write | Zone 2 auto mode heating temperature setting |  | x10 | °C
2114 | 0X2114 | S16 | Read/Write | Room temperature setting |  | x10 | °C | [7 empty] | Yes | target_temperature.floor (weergave)

## HA Integration
HA Type | Entity Name | Source / Logic | Notes / Mapping
binary_sensor | WP Oil return actief | sensor.wp_system_status_bits bit0 | Reg 38 bit 0
binary_sensor | WP Defrost actief | sensor.wp_system_status_bits bit1 | Reg 38 bit 1
binary_sensor | WP Anti-freezing actief | sensor.wp_system_status_bits bit2 | Reg 38 bit 2
binary_sensor | WP Desinfectie actief | sensor.wp_system_status_bits bit4 | Reg 38 bit 4
binary_sensor | WP Buiten temp te laag | sensor.wp_system_status_bits bit11 | Reg 38 bit 11 (compressor geblokkeerd)
binary_sensor | WP Compressor draait | sensor.wp_compressor_frequentie > 0 | Afgeleid van Reg 79
template_sensor | WP DeltaT | aanvoer - retour | Reg 43 - Reg 42 (°C)
template_sensor | WP Thermisch vermogen | 1.163 * flow * DeltaT | kW; uit Reg 64 + DeltaT
template_sensor | WP COP | Q_kW / P_kW | Q van WP, P van extern (Aurora III Pro vermogenmeter)
select | Warmtepomp stille modus | Read/write op Reg 2103 | 3 niveaus: Uit / Stil 1 / Stil 2
climate | Warmtepomp | Reg 43 (current) + Reg 2107 (target) + Reg 2100 (mode) | min=18, max=50, step=1, modes: heat/auto/cool
counter | wp_starts | Triggert op compressor on | Per-uur utility_meter
history_stats | WP Draaitijd laatste 24u | Compressor draait state=on | Sliding window 24u
automation | WP Start teller | Compressor off→on | increment counter
select (uitgebr. YAML) | Warmtepomp zone besturing | Read/write op Reg 2101 | 0 alles uit / 1 zone 1 / 2 zone 2 / 3 alles aan
switch (uitgebr. YAML) | WP Tapwater | Read/write op Reg 2102 | 0 uit / 1 aan
switch (uitgebr. YAML) | WP Geforceerde elektrische bijverwarming | Read-modify-write Reg 2103 bit 3 | Overige bits behouden
number (uitgebr. YAML) | WP Tapwater setpoint | Write Reg 2105 (x10) | 30-60 °C
number (uitgebr. YAML) | WP Ruimtetemperatuur setpoint | Write Reg 2114 (x10) | 16-28 °C; mogelijk niet zonder thermostaat
binary_sensor (uitgebr. YAML) | WP Tapwatermodus actief | Reg 9 bit 2 | Effectieve modus
binary_sensor (uitgebr. YAML) | WP Desinfectie ingeschakeld | Reg 2103 bit 6 | Alleen lezen
binary_sensor (uitgebr. YAML) | WP E-storing / P-beveiliging actief | Reg 90/91, 96/97 > 0 | Bitvelden; alleen eerste 32 codes
template_sensor (uitgebr. YAML) | WP Verwarmings- / Koelvermogen | 1.163 × flow × ΔT | 0 bij ontdooien, stilstand of flow < 0.3 m³/h

## Discrepancies & Notes
Type | Register / Item | Observation | Explanation / Action | Severity | Status app 1.9.3
Spec typo? | Reg 16 | Scale=x1, unit=°C | Vermoedelijk x10 (Z1 auto cooling upper limit). Andere upper/lower limits zijn x10. Verifiëren met fysieke meting. | Medium | Open; app gebruikt x10.
Spec typo? | Reg 27 | Scale=x1, unit=°C | Vermoedelijk x10 (Z2 auto cooling lower limit). Verifiëren. | Medium | Open; app gebruikt x10.
Spec typo? | Reg 67 | Scale=x1, unit=°C | Vermoedelijk x10 (Z1 climate curve heating set temp). Verifiëren. | Medium | Open; app gebruikt x10 zoals HA (@verify), alleen lezen.
Spec typo? | Reg 2109 | Scale=x1, unit=°C | Vermoedelijk x10 (Z1 auto heating temp setting). Belangrijk: dit is een writable register. Verifiëren VÓÓR schrijven. | High | Schrijven in de app geblokkeerd tot verificatie.
Spec gap | Reg 64 | Scale=NaN, unit=m³/h | YAML gebruikt scale=0.1 (komt uit Reg 63 dat x10 is). Spec is incompleet — datasheet/fabrikant raadplegen. | Medium | App: x0.1 m³/h, getoond in L/min (@verify).
Spec gap | Reg 61 | Scale=NaN, unit=Bar | YAML gebruikt scale=0.1. Aannemelijk maar niet bevestigd in spec. | Low | App: x0.1 bar, alleen dashboard.
Spec gap | Reg 86 | Scale=NaN, unit=kPa (high pressure) | Geen scale opgegeven. Bij gebruik eerst kalibratie nodig. | Low | App: x1 kPa (adlar_high_pressure, @verify).
Bit-encoding | Reg 38 | System status bitmask | YAML decoded 5 van mogelijk 16 bits. Volledige bitdefinitie staat niet in spec — alleen via reverse engineering. | Medium | Ongewijzigd: 5 bits bekend.
Bit-encoding | Reg 2103 | Additional function A | Silent mode in bits 4-5. Andere bits onbekend — voorzichtigheid bij schrijven (huidige YAML preserveert via 'cleared'). | Medium | Opgelost: officiële map documenteert bit 3, 4-5 en 6; overige bits gereserveerd.
Naming | Reg 48 vs 49 | Beide heten 'T3' | Reg 48=Solar water heating T3, Reg 49=Outdoor unit coil T3. Verschillende sensoren met dezelfde labelnaam in spec. | Low | —
Encoding | Reg 9 (Effective mode) | Bitmask: bit0=cooling, bit1=heating, bit2=DHW | Read-only configuratie-info — handig voor capability discovery in HA. | Info | In gebruik: adlar_dhw_active (bit 2).
Encoding | Reg 102/103 | Current/Actual operation mode | Spec geeft niet de enum-waarden. Loggen tijdens gebruik om mapping vast te stellen. | High | Opgelost: officiële map documenteert de indeling per zone en tapwater.
HA vs map | Reg 39 | HA: 'externe vorstbeveiliging / extern ontdooien' | Map: aanvraag externe warmtebron tijdens vorstbeveiliging / ontdooien (alleen hybride). App volgt de map. | Low | Gecorrigeerd in 1.9.3
Spec tegenstrijdig | Reg 63 | Titel 'percentage', maar schaal x10 en eenheid m³/h; HA leest % x1 | App volgt de map (x0.1 m³/h) met @verify. Alleen dashboard. | Low | Gecorrigeerd in 1.9.3
HA vs map | Reg 101 | HA-YAML leest de doelmodus uit Reg 101 | Map: Reg 101 = P81-P96, doelmodus staat in Reg 102. App volgt de map. | Medium | Opgelost
Beperking | Reg 2103 bits 4-5 | Stille modus niveau 2 alleen voor R290-warmtepompen | App weigert niveau 2 tenzij Reg 7 = R290. | Medium | Ingevoerd in 1.9.3
Nieuw | Reg 2101 | Zonebesturing 0 alles uit … 3 alles aan | Gebruikt als aan/uit; schrijven alleen met experimentele instelling. | High | Hardwaretest door testgebruikers
Encoding | Reg 90-101 | Map: 'bit by bit operation' | App decodeert per bit (E03, P17) sinds 1.9.0. | Info | Opgelost

## Coverage & Roadmap
Status | Register | Description | Why useful | Priority | Status app 1.9.3
In use | 12 registers | Zie 'Register Map (master)' kolom 'In YAML?' | Operationeel | — | Zie tabblad 'Status app 1.9.3'
Recommended | Reg 46 | DHW water tank temperature TZ2 | Boilertemperatuur monitoren | High | In app: measure_temperature.dhw
Recommended | Reg 2102 | DHW mode on/off (writable) | Bediening warmtapwater vanuit HA | High | In app: adlar_dhw_enabled + flowkaart
Recommended | Reg 2105 | DHW water temperature setting (writable) | DHW setpoint via HA aansturen | High | In app: target_temperature.dhw (begrensd door 3-14/15)
Recommended | Reg 56 | Target outlet setting temperature TOut | Validatie van curve/aansturing — werkelijke target | High | Gelezen; alleen dashboard
Recommended | Reg 86 | High pressure | Veiligheid en performance-monitoring koudemiddelcircuit | Medium | In app: adlar_high_pressure
Recommended | Reg 87 | Low pressure | Idem — diagnose laaglast / vorming | Medium | In app: adlar_low_pressure
Recommended | Reg 52 | Discharge temperature TP | Compressor-gezondheid | Medium | In app: measure_temperature.exhaust
Recommended | Reg 53 | Suction temperature TH | Superheat-berekening (samen met TP en LP) | Medium | In app: measure_temperature.suction
Recommended | Reg 49 | Outdoor unit coil temperature T3 | Defrost-strategie analyseren | Medium | In app: measure_temperature.outer_coil
Recommended | Reg 102/103 | Operation modes | Daadwerkelijke vs gevraagde modus — feedback | Medium | Gelezen; indeling gedocumenteerd, niet gedecodeerd
Recommended | Reg 90-95 | Error codes E01-E96 | Storingsmonitoring → notification automation | High | In app: bitveld → E-codes, alarm, flowtrigger
Recommended | Reg 96-101 | Protection codes P01-P96 | Beveiligingsstatus → diagnose | Medium | In app: bitveld → P-codes
Recommended | Reg 70 | EEV opening (steps) | Regelgedrag expansieventiel | Low | In app: adlar_eev_step
Recommended | Reg 74-77 | AC voltage/current, DC bus, compressor current | Eigen vermogensmeting i.p.v. externe Aurora III Pro | Medium | In app: measure_voltage/current/power, comp_phase; 3-76 alleen dashboard
Conditional | Reg 47, 2110-2113 | Zone 2 temperatures and setpoints | Alleen relevant bij 2-zone installatie | Conditional | Reg 47 → measure_temperature.zone2; 2110-2113 alleen dashboard
Discovery | Reg 0-9, 34-37 | Capabilities & terminal types | Eenmalig uitlezen voor capability discovery in integratie | Low | In app: eenmalig gelezen; 3-2, 3-7 en 3-9 in gebruik
Skip | Reserved registers (24, 25, 32, 33, 54, 55, 57-59, 65, 71, 73, 82-85, 88, 89, 104-109) | Reserved/Reserved | Geen functie volgens spec | —