## Parameters
Installer code | 1212
Order number | Code | State | Default | Minimum | Maximum | Setting interval | Unit
1.1 | Ta | Temperature difference between target LWT and real LWT for startup heat pump | 2 | 1 | 5 | 1 | °C
1.2 | a | DeltaT between the target LWT and real LWT for restarting | 3 | 1 | 10 | 1 | °C
1.3 | Mp | Select priority mode | 0 | 0 | 2 | 1 | /
1.4 | T4L | Minimum ambient temp. of compressor operation for heating and hot water | -25 | -40 | -21 | 1 | °C
1.5 | PUMP_TYPE | Internal DC pump type | DC | DC | AC | 1 | /
1.6 | SB-PWMout | Standby DC pump output | 35 | 10 | 100 | 1 | %
1.7 | RUN-PWMout | Minimum DC pump operation output | 40 | 30 | 100 | 1 | %
1.8 | WPS | Enable or disable water pressure detect, 1=Enable, 0=Disable | 1 | 0 | 1 | 1 | /
1.9 | TH4 | Enable or disable chassis heater, 1=Enable, 0=Disable | 1 | 0 | 1 | 1 | /
2.1 | Tb | Temperature difference between target hot water and real tank water for startup heat pump | 5 | 2 | 15 | 1 | °C
2.2 | Tx | Target disinfect temperature | 65 | 55 | 75 | 1 | °C
2.3 | Teh | Ambient temperature of tank heater startup | 4 | -10 | 40 | 1 | °C
2.4 | Td | Disinfect running time | 30 | 20 | 120 | 1 | MIN
2.5 | TANK HEATER | Enable or disable tank heater, NON=Disable, YES=Enable | YES | NON | YES | / | /
2.6 | P_d_DHW | Enable or disable tank pump control, NON=Disable, YES=Enable | NON | NON | YES | / | /
2.7 | P_d_DIS | Enable or disable tank pump in disinfect mode, NON=Disable, YES=Enable | YES | NON | YES | / | /
2.8 | P_d_TIME KEEP | Enable or disable tank pump operation timing, NON=Disable, YES=Enable | YES | NON | YES | / | /
2.9 | t_P_d_on | Tank pump ON time | 5 | 5 | 120 | 1 | MIN
3.1 | ZONE A HEAT-TYPE | Zone A heating terminal device type, 0=FCU, 1=RAD, 2=FLH | RAD | FCU | FLH | 1 | /
3.2 | ZONE B HEAT-TYPE | Zone B heating terminal device type, 0=FCU, 1=RAD, 2=FLH | FLH | FCU | FLH | 1 | /
3.3 | HIGH TEMP HEAT OFF | Enable or disable high temperature shutdown, 0=Disable, 1=Enable | 0 | 0 | 1 | 1 | /
3.4 | HD | 0=Disable IPH, 1=Enable IPH | 1 | 0 | 1 | 1 | /
3.5 | T4h | Maximum shutdown T4 temperature | 24 | 10 | 30 | 1 | °C
3.6 | T4g | Ambient temperature of Enabling IPH or AHS | -10 | -20 | 20 | 1 | °C
3.7 | H-PUMP | DC pump standby speed for heating | 3 | 0 | 3 | 1 | /
3.8 | t_T4_FRESH_H | Refresh time of climate curve for heating | 30 | 10 | 360 | 10 | MIN
3.9 | T4_ha1 | Auto climate curve ambient temp. 1 for heating | -5 | -25 | 35 | 1 | °C
3.10 | T4_ha2 | Auto climate curve ambient temp. 2 for heating | 7 | -25 | 35 | 1 | °C
3.11 | SPTch_set1 | Auto climate curve target temp. 1 for heating | 35 | 25 | 60 | 1 | °C
3.12 | SPTch_set2 | Auto climate curve target temp. 2 for heating | 28 | 25 | 60 | 1 | °C
4.1 | ZONE A COOL TYPE | Zone A cooling terminal device type, 0=FCU, 1=RAD, 2=FLH | FCU | FCU | FLH | 1 | /
4.2 | ZONE B COOL TYPE | Zone B cooling terminal device type, 0=FCU, 1=RAD, 2=FLH | FCU | FCU | FLH | 1 | /
4.3 | C-Pump | DC pump standby speed for cooling | 3 | 0 | 3 | 1 | /
4.4 | t_T4_FRESH_C | Refresh time of climate curve for cooling | 30 | 30 | 360 | 10 | MIN
4.5 | T4_ca1 | Auto climate curve ambient temp. 1 for cooling | 25 | -5 | 46 | 1 | °C
4.6 | T4_ca2 | Auto climate curve ambient temp. 2 for cooling | 35 | -5 | 46 | 1 | °C
4.7 | SPTcc_set1 | Auto climate curve target temp. 1 for cooling | 16 | 5 | 25 | 1 | °C
4.8 | SPTcc_set2 | Auto climate curve target temp. 2 for cooling | 10 | 5 | 25 | 1 | °C
5.1 | AUTO HEAT MAX T4 | Maximum ambient temp. of auto-heating mode | 17 | 10 | 17 | 1 | °C
5.2 | AUTO COOL MIN T4 | Minimum ambient temp. of auto-cooling mode | 25 | 20 | 29 | 1 | °C
6.1 | ZONE TYPE | Two zones, 0=single zone, 2=dual zone | 1 | 1 | 2 | 1 | /
6.2 | SINGLE ZONE OPERATION | Single zone target temperature type | 0 | 0 | 3 | 1 | /
6.3 | DUAL ZONE OPERATION | Dual zone target temperature type (2 and 6 for reserved) | 0 | 0 | 7 | 1 | /
7.1 | ROOM THERMOSTAT | Room thermostat type, 0=NON=without room thermostat, 1=MODE SET, 2=ONE ZONE, 3=TWO ZONES | 0 | 0 | 3 | 1 | /
7.2 | SINGLE ZONE RT SET | Target temperature type on ROOM THERMOSTAT = MODE SET or ONE ZONE | 0 | 0 | 1 | 1 | /
7.3 | DUAL ZONE RT SET | Target temperature type on ROOM THERMOSTAT = TWO | 0 | 0 | 3 | 1 | /
8.1 | dTro | dTro is the bias of room temperature to start and stop the heat pump. When dTro=1 and room target=20°C, heat pump starts below 21°C and goes standby below 19°C. | 1 | 0.5 | 3 | 0.5 | °C
9.1 | TE1 | Enable or disable TE1, NON=Disable, YES=Enable | NON | NON | YES | / | /
10.1 | TZ2 | Enable or disable TZ2, NON=Disable, YES=Enable | NON | NON | YES | / | /
10.2 | t_SV3_ON | SV3 on time | 5 | 0 | 0 | 1 | MIN
10.3 | t_SV3_OFF | SV3 off time | 2 | 0 | 120 | 1 | MIN
10.4 | dT_SV3_ON | Temperature difference for SV3 ON | 5 | 0 | 10 | 1 | °C
10.5 | dT_SV3_OFF | Temperature difference for SV3 OFF | 0 | -10 | 0 | 1 | °C
11.1 | dTso | Temperature difference for startup solar pump | 10 | 2 | 20 | 1 | °C
11.2 | tso | Solar pump running time | 30 | 0 | 90 | 1 | MIN
11.3 | Solar_Type | Solar type, 0=NON, 1=Solar temp. sensor, 2=SL1SL2 | 0 | 0 | 2 | 1 | /
11.4 | AHS_Type | 0=AHS Disable, 1=AHS with only heating, 2=AHS both heating and DHW | 0 | 0 | 2 | 1 | /
12.1 | t_SG_Block | Smart Grid block time | 2 | 0 | 24 | 1 | Hr
12.2 | IP | Address code | 251 | 1 | 255 | 1 | /
12.3 | Energy Information | Enable: to display; Disable: not to display | Enable | Enable | Disable | / | /

## Function Descriptions
Previous No. | Parameter | Value | Function
1.3 | Mp | 0 | Hot water priority
1.3 | Mp | 1 | Space heating/cooling priority
1.3 | Mp | 2 | Preempty
1.4 | T4L |  | If ambient temperature less than T4L, do not turn on heat pump, but can turn on backup heater or AHS
1.5 | PUMP_TYPE | AC | AC means internal water pump is alternating current
1.5 | PUMP_TYPE | DC | DC means internal water pump is PWM
1.6 | SB-PWMout |  | Means PWM pump running speed when heat pump is standby mode in which the compressor shuts down because of getting a target temperature
1.7 | RUN-PWMout |  | PWM pump must not operate below this speed when PWM pump is in speed adjustment
12.2 | IP |  | Heat pump address code in group controller
9.1 | TE1 |  | To activate temperature sensor mounted on top of buffer tank in cascade mode, but the function is for reserved
10.1 | TZ2 |  | To activate Zone 2 inlet temperature sensor function to get a low zone 2 target water temperature