## Modbus Point List
RS-485 ModbusRTU :251
Mother board address: 251
Baud rate: 9600bps
Data bits: 8 bits
Parity bit: None Parity
Stop bit: 2 stop bit
CRC-16 Checkout: Modbus Modbus format
3X;4X
Data in area 3X can be read only, data in 4X can be read and written
Function codes supported: 0X03, 0X04, 0X06, 0X10
Address of register | Data type | Data content | Description
3X0000 | U16 | Total number of addresses | Since 3X0000 (including 3X0000)
3X0001 | U16 | Third party thermostat controller type | 0: without third party thermostat 1: with third party thermostat(single zone control: on/off and mode change) 2: with third party thermostat(single zone control: on/off) 3: with third party thermostat(two zones control: on/off)
3X0002 | U16 | Without third party thermostat single zone or two zones control | 0: 1: 0: single zone, 1: two zones
3X0003 | U16 | Without third party thermostat for single zone control | 0: the setting water temperature works as the target temperature to turn on/off the unit 1: the climate curves setting water temperature works as the target temperature to turn on/off the unit 2 reserved: the setting water temperature works as the target temperature and room setting temperature is used to turn on/off the unit 3: the climate curves setting water temperature works as the target temperature and room setting temperature works to turn on/off the unit
3X0004 | U16 | Without third party thermostat for two zones control | Complex multi-zone control modes (0-7)
3X0005 | U16 | With thermostat single zone control | 0: the manual setting water temperature works as the target temperature to turn on/off the unit 1: the climate curves setting water temperature works as the target temperature to turn on/off the unit
3X0006 | U16 | With thermostat two zones control | 0: both zone 1/2: the setting water temperature works as the target temperature to turn on/off the unit 1: zone 1: the manual setting water temperature... 2: zone 1: climate curves setting water temperature... 3: both zone 1/2: the climate curves setting water temperature works as the target temperature to turn on/off the unit
3X0007 | U16 | Refrigerant type | 0: R32 R32 Series 1: R290 R290 Series
3X0008 | U16 | Unit type | Bit[5:1] Bit[0](1)
3X0009 | U16 | Effective mode | Bit[15:3]: Reserved Bit[2](1): DHW mode effective or not(1 means effective) Bit[1](1): Heating mode effective or not(1 means effective) Bit[0](1): Cooling mode effective or not(1 means effective)
3X0010 | S16 | Zone 1 cooling mode temperature setting upper limit
3X0011 | S16 | Zone 1 cooling mode temperature setting lower limit
3X0012 | S16 | Zone 1 heating mode temperature setting upper limit
3X0013 | S16 | Zone 1 heating mode temperature setting lower limit
3X0014 | S16 | Zone 1 DHW mode temperature setting upper limit
3X0015 | S16 | Zone 1 DHW mode temperature setting lower limit
3X0016 | S16 | Zone 1 auto cooling temperature setting upper limit | For example: 123 means 123 degree celsius
3X0017 | S16 | Zone 1 auto cooling temperature setting lower limit
3X0018 | S16 | Zone 1 auto heating temperature setting upper limit
3X0019 | S16 | Zone 1 auto heating temperature setting lower limit
3X0020 | S16 | Zone 2 cooling mode temperature setting upper limit
3X0021 | S16 | Zone 2 cooling mode temperature setting lower limit
3X0022 | S16 | Zone 2 heating mode temperature setting upper limit
3X0023 | S16 | Zone 2 heating mode temperature setting lower limit
3X0024 | U16 | Reserved
3X0025 | U16 | Reserved
3X0026 | S16 | Zone 2 auto mode cooling temperature setting upper limit
3X0027 | S16 | Zone 2 auto mode cooling temperature setting lower limit | For example: 123 means 123 degree celsius
3X0028 | S16 | Zone 2 auto mode heating temperature setting upper limit
3X0029 | S16 | Zone 2 auto mode heating temperature setting lower limit
3X0030 | S16 | Room temperature setting upper limit | For example: 123 means 12.3 degree celsius
3X0031 | S16 | Room temperature setting lower limit
3X0032 | U16 | Reserved
3X0033 | U16 | Reserved
3X0034 | U16 | Zone 1 terminal type for cooling
3X0035 | U16 | Zone 1 terminal type for heating | 0: FCU, 1: Radiator, 2: Floor heating circuit
3X0036 | U16 | Zone 2 terminal type for cooling
3X0037 | U16 | Zone 2 terminal type for heating
3X0038 | U16 | System status | B15-B12: Reserved B11: Ambient temp. too low, compressor can not be started B10-B8: Reserved B7-B5: Reserved B4: Disinfection mode is running B3: Reserved B2: Anti-freezing mode is running B1: Defrosting mode is running B0: Oil return mode is running 0: off, 1: on
3X0039 | U16 | Request external heating source (only for hybrid solution) | B15-B4: Reserved B3: Reserved B2: Reserved B1: Request external heating source during defrosting mode B0: Request external heating source during anti-freezing mode 0: off, 1: on
3X0040 | S16 | Room temperature Tldr
3X0041 | S16 | Total leaving water temperature TC (after auxiliary gas boiler heaters)
3X0042 | S16 | Inlet water temperature TA
3X0043 | S16 | Leaving water temperature TE1
3X0044 | S16 | Buffer tank upper part temperature TE2 (reserved)
3X0045 | S16 | Buffer tank lower part temperature TW
3X0046 | S16 | DHW water tank temperature TZ2 | For example: 123 means 12.3 degree celsius
3X0047 | S16 | Zone 2 mixing station inlet water temperature Tso
3X0048 | S16 | Solar water heating temperature T3
3X0049 | S16 | Outdoor unit coil temperature T3
3X0050 | S16 | Ambient temperature T4
3X0051 | S16 | Outlet temperature of the EXV valve T5
3X0052 | S16 | Discharge temperature TP
3X0053 | S16 | Suction temperature TH
3X0054 | S16 | Reserved
3X0055 | S16 | Reserved
3X0056 | S16 | Target outlet setting temperature TOut
3X0057 | U16 | Reserved
3X0058 | U16 | Reserved
3X0059 | U16 | Reserved
3X0060 | U16 | Inlet water pressure (reserved) | For example: 123 means 12.3Bar
3X0061 | U16 | Outlet water pressure
3X0062 | U16 | PWM - Percentage of output PWM of DC water pump | For example: 123 means 123%
3X0063 | U16 | PWM - Percentage of feedback PWM of DC water pump | For example: 123 means 12.3m3/h
3X0064 | U16 | Actual water flow of the DC pump
3X0065 | U16 | Reserved
3X0066 | S16 | Zone 1 climate curve cooling set temperature
3X0067 | S16 | Zone 1 climate curve heating set temperature | For example: 123 means 123 degree celsius
3X0068 | S16 | Zone 2 climate curve cooling set temperature
3X0069 | S16 | Zone 2 climate curve heating set temperature
3X0070 | U16 | EEV Main EEV open degree | For example: 123 means 123 steps
3X0071 | U16 | EEV Auxiliary EEV open degree Reserved
3X0072 | U16 | 1 Speed of No.1 DC fan | For example: 123 means 123 Revolutions per minute
3X0073 | U16 | 2 Reserved
3X0074 | U16 | AC input voltage | For example: 123 means 123V
3X0075 | U16 | AC input current | For example: 123 means 12.3A
3X0076 | U16 | DC bus voltage | For example: 123 means 123V
3X0077 | U16 | Compressor current | For example: 123 means 12.3A
3X0078 | U16 | Compressor target frequency
3X0079 | U16 | Compressor actual frequency | For example: 123 means 123Hz
3X0080 | U16 | Main water pump on/off status (unit internal circulation water pump) | 0: off, 1: on
3X0081 | U16 | Four way valve on/off status | 0: off, 1: on
3X0082 | U16 | Reserved
3X0083 | U16 | Reserved
3X0084 | U16 | Reserved
3X0085 | U16 | Reserved
3X0086 | U16 | High pressure
3X0087 | U16 | Low pressure | For example: 123 means 123kpa
3X0088 | U16 | Reserved
3X0089 | U16 | Reserved
3X0090 | U16 | E01-E16 | E01-E96 bit by bit operation 3X0090 bit0 1E01 For example, if the bit0 of 3X0090 is 1, E01 is the error code 3X0091 bit1 1E18 For example, if the bit1 of 3X0091 is 1, E18 is the error code
3X0091 | U16 | E17-E32
3X0092 | U16 | E33-E48
3X0093 | U16 | E49-E64
3X0094 | U16 | E65-E80
3X0095 | U16 | E81-E96
3X0096 | U16 | P01-P16 | P01-P96 bit by bit operation 3X0096 bit0 1P01 For example, if the bit0 of 3X0096 is 1, P01 is the error code 3X0097 bit1 1P18 For example, if the bit0 of 3X0097 is 1, P18 is the error code
3X0097 | U16 | P17-P32
3X0098 | U16 | P33-P48
3X0099 | U16 | P49-P64
3X0100 | U16 | P65-P80
3X0101 | U16 | P81-P96
3X0102 | U16 | Current target operation mode | B15-B9: Auto target mode 0X01: Cooling mode 0X02: Heating mode 0X11-B8: DHW target mode 0X00: Standby mode 0X08: DHW mode B7-B4: Two zones control: zone 2 air conditioner target mode 0X00: Standby mode 0X01: Cooling mode 0X02: Heating mode B3-B0: Two zones control: zone 1 air conditioner target mode One zone control: air conditioner target mode 0X00: Standby mode 0X01: Cooling mode 0X02: Heating mode
3X0103 | U16 | Actual operation mode | B15-B9: Reserved B11-B8: DHW operation mode 0X00: Standby 0X08: DHW mode B7-B4: Two zones control: zone 2 air conditioner operation mode 0X00: Standby 0X01: Cooling 0X02: Heating B3-B0: Two zones control: zone 1 air conditioner operation mode One zone control: air conditioner operation mode 0X00: Standby 0X01: Cooling 0X02: Heating
3X0104 | U16 | Reserved
3X0105 | U16 | Reserved
3X0106 | U16 | Reserved
3X0107 | U16 | Reserved
3X0108 | U16 | Reserved
3X0109 | U16 | Reserved
4X2100 | U16 | Air condition modes | 1: Cooling mode 2: Heating mode 4: Auto mode
4X2101 | U16 | Air condition modes (zone control) | 0: All off 1: Zone 1 on, zone 2 off 2: Zone 1 off, zone 2 on 3: All on
4X2102 | U16 | DHW mode on/off | 0: DHW off 1: DHW on
4X2103 | U16 | Additional function A | Bit[15-8]: Reserved Bit[7]: Reserved Bit[6]: Disinfection mode Bit[5-4]: Silent mode 0: Silent mode off 1: Silent mode level one 2: Silent mode level two (only for R290 heat pumps) Bit[3]: Forced electrical heater Bit[2]: Reserved Bit[1]: Reserved Bit[0]: Reserved 0: off, 1: on
4X2104 | U16 | B() Additional function A (Reserved) | 0: off 1: on
4X2105 | S16 | DHW mode water temperature setting
4X2106 | S16 | Zone 1 cooling mode temperature setting
4X2107 | S16 | Zone 1 heating mode temperature setting
4X2108 | S16 | Zone 1 auto mode cooling temperature setting
4X2109 | S16 | Zone 1 auto mode heating temperature setting | For example: 123 means 123 degree celsius
4X2110 | S16 | Zone 2 cooling mode temperature setting
4X2111 | S16 | Zone 2 heating mode temperature setting
4X2112 | S16 | Zone 2 auto mode cooling temperature setting
4X2113 | S16 | Zone 2 auto mode heating temperature setting
4X2114 | S16 | Room temperature setting