## Sheet1
Name | Address | Quantity | DataType | FuncCode | ByteOrder | WordOrder | Scale | Offset | Unit
Running Status 1 [MACHINE_RUN=0x4000] | 0 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Running Status 2 [CONTROLLER_ON_OFF=0x0400] | 1 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Fault State 1 [geen storingen] | 2 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Fault State 2 [geen storingen] | 3 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Fault State 3 [geen storingen] | 4 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Sys1 Fault State 1 [geen storingen] | 5 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Sys1 Fault State 2 [geen storingen] | 6 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Sys1 Drive Fault 1 [geen storingen] | 7 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Sys1 Drive Fault 2 [geen storingen] | 8 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Sys1 Drive Fault 3 [geen storingen] | 9 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Relay Output 1 [MAIN_CIRCULATING_PUMP=0x0040] | 25 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Relay Output 2 [COMP1=0x01¦4WAY=0x08¦FAN1=0x20 → 0x29=41] | 26 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Relay Output 3 [geen aux relais actief] | 27 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Relay Output 4 [geen zone-pompen actief] | 28 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Switch Port State 1 [WATER_FLOW_SWITCH=0x0100 → OK] | 29 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Switch Port State 2 [HP_SW1=0x80¦LP_SW1=0x100 → druken OK] | 30 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Switch Port State 3 | 31 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Switch Port State 4 | 32 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Compressor Target Freq [55 Hz] | 39 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Compressor Running Freq [55 Hz] | 64 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
Fan Running Speed [900 RPM = 60 Hz × 15] | 65 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | RPM
EEV Open Step [280 P] | 66 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | P
EVI Valve Open Step [0 P, geen EVI actief] | 67 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | P
AC Input Voltage [232 × 0.99 = 229.7 V ≈ 230 V] | 68 | 1 | uint16 | 3 | big_endian | big_endian | 0.99 | 0 | V
AC Input Current [65 × 0.1 = 6.5 A raw; cal.curve → ~5.5 A werkelijk] | 69 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | A
Compressor Phase Current [58 × 0.1 = 5.8 A] | 70 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | A
Compressor IPM Temp [350 × 0.1 = 35.0 °C] | 71 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
High Pressure Sat Temp [450 × 0.1 = 45.0 °C] | 72 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Low Pressure Sat Temp [int16: -50 = -5.0 °C (65536-50=65486)] | 73 | 1 | int16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T1 Ambient Temp [70 × 0.1 = 7.0 °C] | 74 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T2 Outer Coil Temp [int16: -20 = -2.0 °C (65536-20=65516)] | 75 | 1 | int16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T3 Inner Coil Temp [380 × 0.1 = 38.0 °C] | 76 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T4 Suction Temp [int16: -25 = -2.5 °C (65536-25=65511)] | 77 | 1 | int16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T5 Exhaust Temp [750 × 0.1 = 75.0 °C] | 78 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T6 Water Inlet (return) [310 × 0.1 = 31.0 °C] | 79 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T7 Water Outlet (aanvoer) [380 × 0.1 = 38.0 °C] | 80 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T8 Economizer Inlet [120 × 0.1 = 12.0 °C] | 81 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
T9 Economizer Outlet [180 × 0.1 = 18.0 °C] | 82 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Device Tooling No | 83 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
DHW Tank Temp [480 × 0.1 = 48.0 °C, warmwaterboiler standby] | 84 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Plate HX Exhaust Temp [600 × 0.1 = 60.0 °C] | 85 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Drive Manufacturer Code [1] | 86 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Water Pump Speed [75 %PWM] | 87 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | %
Water Flow [15 L/min] | 88 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | L/min
DHW Return Water Temp [400 × 0.1 = 40.0 °C] | 89 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Unit Input Voltage [230 V] | 90 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | V
Unit Input Current [652 × 0.01 = 6.52 A → 1500 W / 230 V] | 91 | 1 | uint16 | 3 | big_endian | big_endian | 0.01 | 0 | A
Unit Input Power [150 × 0.01 = 1.50 kW] | 92 | 1 | uint16 | 3 | big_endian | big_endian | 0.01 | 0 | kW
Total Energy Consumption [1847 kWh] | 93 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | kWh
Solar Water Heater Temp [0 = geen sensor/zonne-energie] | 114 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Zone 2 Temp [200 × 0.1 = 20.0 °C] | 115 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Buffer Tank Temp [350 × 0.1 = 35.0 °C] | 116 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Total Water Outlet Temp [380 × 0.1 = 38.0 °C] | 117 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
B Phase Input Voltage [230 V] | 118 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | V
B Phase Input Current [650 × 0.01 = 6.50 A] | 119 | 1 | uint16 | 3 | big_endian | big_endian | 0.01 | 0 | A
C Phase Input Voltage [231 V] | 120 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | V
C Phase Input Current [640 × 0.01 = 6.40 A] | 121 | 1 | uint16 | 3 | big_endian | big_endian | 0.01 | 0 | A
Smart Grid Status [0 = normaal] | 122 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Zone 2 Mixing Valve Opening [0 %] | 123 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | %
Zone 1 Mixing Temp [380 × 0.1 = 38.0 °C] | 124 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Zone 1 Mixing Valve Opening [0 %] | 125 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | %
P00 T1 Ambient Temp Sensor [0 = enabled] | 256 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P01 High Voltage Switch [0 = enabled] | 257 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P02 Low Pressure Switch [0 = enabled] | 258 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P03 Water Flow Switch [1 = disabled, externe flowmeter actief] | 259 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P04 Thermal Overload Protection [0 = enabled] | 260 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P05 Linkage Switch [0 = enabled] | 261 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P06 Fan Type [1 = DC] | 262 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P07 High Voltage Lock [0 = 3 locks] | 263 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P08 Low Voltage Lock [0 = 3 locks] | 264 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P09 Exhaust Lock [0 = 3 locks] | 265 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P10 Water Flow Lock [0 = 3 locks] | 266 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P11 High Pressure Protection [115 °C condensatieTemp] | 267 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P12 High Pressure Freq Limit [110 °C = P11 − 5] | 268 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P13 Low Pressure Protection [int16: -30 °C (65536-30=65506)] | 269 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0 | °C
P14 Low Pressure Freq Limit [int16: -25 °C (65536-25=65511)] | 270 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0 | °C
P15 Exhaust Temp Protection [120 °C] | 271 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P16 Exhaust Temp Freq Limit [110 °C = P15 − 10] | 272 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P30 Defrost Mode [0 = Smart] | 286 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P50 Cooling Target Freq Constant A | 306 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0
P51 Cooling Min Freq [25 Hz] | 307 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P52 Cooling Target Freq Upper [80 Hz] | 308 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P53 Cooling Target Freq Lower [30 Hz] | 309 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P54 Heating Target Freq Constant B | 310 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0
P55 Heating Target Freq Upper [90 Hz] | 311 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P56 Heating Target Freq Lower [25 Hz] | 312 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P57 Heating Min Freq >0°C [25 Hz — COP-geoptimaliseerd] | 313 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P58 Heating Min Freq −10~0°C [35 Hz] | 314 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P59 Heating Min Freq <−10°C [45 Hz] | 315 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P60 DHW Target Freq Constant | 316 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0
P61 DHW Target Freq Upper [80 Hz] | 317 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P62 DHW Target Freq Lower [25 Hz] | 318 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P63 DHW Min Freq >0°C [25 Hz] | 319 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P64 DHW Min Freq −10~0°C [35 Hz] | 320 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P65 DHW Min Freq <−10°C [45 Hz] | 321 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P88 Silent Mode Compressor Freq [35 Hz] | 344 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P89 Silent Mode Fan Freq [30 Hz → 450 RPM] | 345 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | Hz
P101 Pump Control Mode [1 = DC/PWM] | 357 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P114 Nr Compressors [1 = single] | 370 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P115 Model Selection [0 = double supply] | 371 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P116 Temp Control Mode [0 = inlet T6 (retour)] | 372 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P117 Antifreeze Ambient Temp [5 °C] | 373 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P118 Antifreeze Outlet Water [3 °C] | 374 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | °C
P119 Refrigerant Type [2 = R32 — Adlar Castra Aurora II] | 375 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P120 Anti-condensation Function [0] | 376 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P164 Energy Level Control [0 = geen beperking] | 420 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P255 Smart Grid [0 = inactief] | 511 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
P256 Smart Grid [0 = inactief] | 512 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | min
Set Cooling Temp [120 × 0.1 = 12.0 °C] | 768 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Set Heating Temp [550 × 0.1 = 55.0 °C] | 769 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Set Hot Water Temp [550 × 0.1 = 55.0 °C] | 770 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Set Floor Heating Temp [500 × 0.1 = 50.0 °C] | 771 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Mode [1 = Heating] | 772 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Main Switch [1 = ON] | 773 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Indoor Temp Setpoint [205 × 0.1 = 20.5 °C] | 774 | 1 | uint16 | 3 | big_endian | big_endian | 0.1 | 0 | °C
Running Mode [0 = Standard] | 775 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Cooling Curve [0 = off] | 787 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Heating Curve [3 = High Temp Curve 3] | 788 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Hot Water Curve [0 = off] | 789 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Floor Heating Curve [0 = off] | 790 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Program Version [130 = V1.3.0] | 864 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Product Type [0 = Commercial Inverter] | 865 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Product Type ID [0 = 2-unit] | 866 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
Protocol Version [130 = coil-support + aparte curve-registers actief] | 867 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
L27 Heating Low Temp Curve DIY [1 = disabled, preset curve actief] | 2064 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
L28 Heating Curve Coeff K [niet actief] | 2065 | 1 | int16 | 3 | big_endian | big_endian | 1 | 0
L29 Heating Curve Constant B [niet actief] | 2066 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
L30 Heating Capacity Statistics [0 = enabled] | 2067 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0
L31 External Pump Flow Rate [15 L/min — klopt met waterflow sensor] | 2068 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | L/min
L32 DHW E-Heater Power [0 W — geen elektrische bijverwarming] | 2069 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | W
L33 Pipe E-Heater 1 Power [0 W] | 2070 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | W
L34 Pipe E-Heater 2 Power [0 W] | 2071 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | W
L35 Heating E-Heater Power [0 W] | 2072 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | W
L36 External Water Pump Power [50 W] | 2073 | 1 | uint16 | 3 | big_endian | big_endian | 1 | 0 | W
Note on E1: 1: Read Coils 2: Read Discrete Inputs 3: Read Holding Registers 4: Read Input Registers