## Tabelle1
Address | Parameter Name | Value | Type
0x0300 | Cooling set temperature | °C | Read-Write
0x0301 | Heating set temperature | °C | Read-Write
0x0302 | Hot water set temperature | °C | Read-Write
0x0303 | Floor heating set temperature | °C | Read-Write
0x0304 | Set mode | 0: cooling 1: heating 2: hot water 3: Floor heating 4: Hot water + cooling 5: Hot water + heating 6: Reserve 7: Hot water + floor heating | Read-Write
0x0305 | On/Off | 0: Power off 1: Power on | Read-Write
0x0306 | Indoor temperature set point | °C | Read-Write
0x0307 | Frequency conversion mode | 0: Standard mode 1: High power mode 2: Silent mode | Read-Write
0x0313 | Cooling curve setting | 0: Off 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 5: Curve 5 6: Curve 6 7: Curve 7 8: Curve 8 | Read-Write
0x0314 | Heating curve setting | 0: Off 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 5: Curve 5 6: Curve 6 7: Curve 7 8: Curve 8 | Read-Write
0x0315 | Hot water curve setting | 0: Off 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 | Read-Write
0x0316 | Floor heating curve setting | 0: Off 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 5: Curve 5 6: Curve 6 7: Curve 7 8: Curve 8 | Read-Write