## Overview
Update Record – Communication Protocol OPxPii TB/TC/TD V1.2.9
Protocol Version | Changer | Modify Date | Modification Explanation
1.0.0 | SenmingWu | 2021-08-11 | first edition
1.0.1 | SenmingWu | 2021-08-12 | Reducing theuseofaddress space
1.0.2 | SenmingWu | 2021-08-14 | Add the read-only parameter for the temperature of the upper and lowerlimits
1.0.3 | SenmingWu | 2021-08-14 | Addtheselection parameters ofambient temperature Modify the description of high-pressure switch and low-pressure switch
1.0.4 | SenmingWu | 2021-08-26 | Addcontrol command of domesticheat pump Addsavecommand offactory parameters Addrelevant parameters of water supply Addmodel setting parameters
1.0.5 | SenmingWu | 2021-08-27 | Add the operating state parameters of the frequency conversion compressor
1.0.6 | SenmingWu | 2021-08-27 | Addupperand lowerlimit parameters' addresses and descriptions
1.0.7 | SenmingWu | 2021-08-28 | Addsystem parameterand operation parameter flag bit selection
1.0.8 | SenmingWu | 2020-08-30 | Adjustthe address ofupper and lowerlimits of temperature setting Adjust the mode to select the address, and put it to the model group address
1.0.9 | SenmingWu | 2021-09-09 | Redefine thedataaccording tothe protocol architecture AddtheLparameter group correspondence
1.1.0 | SenmingWu | 2021-09-22 | Add0x0025Address: Current modeset temperature Add0x0026Address: Hot water’sdefault set temperature
1.1.1 | SenmingWu | 2021-09-22 | Add address 0x0366 to select the temperature displayed at the maininterface
1.1.2 | SenmingWu | 2021-09-27 | Addthewater pump feedback fault mark
1.1.3 | SenmingWu | 2021-09-29 | Change thelocation of 0x0036and0x0035addresses Addaddress 0x0800-0x08FF
1.1.4 | SenmingWu | 2021-10-08 | Addtheswitching ofground heating +hot water mode
1.1.5 | SenmingWu | 2021-10-22 | Addlowwater flowprotection
1.1.6 | SenmingWu | 2021-11-02 | Optimizedomesticmode
1.1.7 | SenmingWu | 2021-11-16 | Add the automatic mode temperature settings,lower refrigeration limit for lower limit value,upper heating limit for upper limit value,add thesettingaddress of theunitassembly number
1.1.8 | SenmingWu | 2021-12-04 | Addthetemperaturecurve selection
1.1.9 | SenmingWu | 2021-12-11 | Addmanual water return/water replenishing/water supply
1.2.0 | SenmingWu | 2022-07-04 | Distinguish oftemp.unit,and add theaddress:0x364
1.2.1 | SenmingWu | 2022-08-26 | Add:1.totalwater out temp.failures 2.parameters
1.2.2 | SenmingWu | 2022-10-11 | Add3address AddtheRWcommand for each coil
1.2.3 | SenmingWu | 2022-10-12 | Addheating curves
1.2.4 | SenmingWu | 2022-11-28 | Addcontent ofthedouble sytstem Addparameters ofdefrost opening anti-freezeinvertal time
V1.2.5 | SenmingWu | 2022-12-24 | Modify notes ofsomeparameters
V1.2.6 | SenmingWu | 2022-12-26 | Modify thecurve
V1.2.7 | SenmingWu | 2022-12-28 | Modify and add someaddresses
V1.2.8 | SenmingWu | 2023-02-14 | Addparameterof pipeelectricity heating
V1.2.9 | SenmingWu | 2023-04-11 | Addsomeparameters
Register Address Space Overview
No | Register Group | Address Range | Access Type | Size
1 | Real-time status & fault | 0x0000 – 0x003F | Read-Only | 64 registers
2 | Real-time data (measurements) | 0x0040 – 0x00FF | Read-Only | 192 registers
3 | Unit system parameters P | 0x0100 – 0x02FF | Read-Write | 512 registers
4 | User parameters | 0x0300 – 0x032F | Read-Write | 48 registers
5 | User orders | 0x0330 – 0x035F | Read-Write | 48 registers
6 | Version information | 0x0360 – 0x036F | Read-Only | 16 registers
7 | Unit system parameters L | 0x0800 – 0x083F | Read-Write | 64 registers
8 | Bit operation instructions (coils) | 0x1000 – 0x10FF | Read-Write | 256 coils

## 1_Status_Fault (0x0000-003F)
1. Real-time Status & Fault Registers (0x0000 – 0x003F) Including: switch port, electric relay, dial switch, fault and other data
Address (hex) | Parameter Name | Range / Format | Default | Access | Note
0x0000 | Running Status 1 | Standard Bits |  | Read-Only
0x0001 | Running Status 2 | Standard Bits |  | Read-Only
0x0002 | Fault State 1 | Standard Bits |  | Read-Only
0x0003 | Fault State 2 | Standard Bits |  | Read-Only
0x0004 | Fault State 3 | Standard Bits |  | Read-Only
0x0005 | System 1 Fault State 1 | Standard Bits |  | Read-Only
0x0006 | System 1 Fault State 2 | Standard Bits |  | Read-Only
0x0007 | System 1 Drive Fault State 1 | Standard Bits |  | Read-Only
0x0008 | System 1 Drive Fault State 2 | Standard Bits |  | Read-Only
0x0009 | System 1 Drive Fault State 3 | Standard Bits |  | Read-Only
0x000A | System 2 Fault State 1 | Standard Bits |  | Read-Only | Refer to 0x0005
0x000B | System 2 Fault State 2 | Standard Bits |  | Read-Only | Refer to 0x0006
0x000C | System 2 Drive Fault State 1 | Standard Bits |  | Read-Only | Refer to 0x0007
0x000D | System 2 Drive Fault State 2 | Standard Bits |  | Read-Only | Refer to 0x0008
0x000E | System 2 Drive Fault State 3 | Standard Bits |  | Read-Only | Refer to 0x0009
0x000F | (System 3 Fault State 1) | Standard Bits |  | Read-Only | Refer to 0x0005
0x0010 | (System 3 Fault State 2) | Standard Bits |  | Read-Only | Refer to 0x0006
0x0011 | (System 3 Drive Fault State 1) | Standard Bits |  | Read-Only | Refer to 0x0007
0x0012 | (System 3 Drive Fault State 2) | Standard Bits |  | Read-Only | Refer to 0x0008
0x0013 | (System 3 Drive Fault State 3) | Standard Bits |  | Read-Only | Refer to 0x0009
0x0014 | (System 4 Fault State 1) | Standard Bits |  | Read-Only | Refer to 0x0005
0x0015 | (System 4 Fault State 2) | Standard Bits |  | Read-Only | Refer to 0x0006
0x0016 | (System 4 Drive Fault State 1) | Standard Bits |  | Read-Only | Refer to 0x0007
0x0017 | (System 4 Drive Fault State 2) | Standard Bits |  | Read-Only | Refer to 0x0008
0x0018 | (System 4 Drive Fault State 3) | Standard Bits |  | Read-Only | Refer to 0x0009
0x0019 | Relay output status 1 | Standard Bits |  | Read-Only
0x001A | Relay output status 2 | Standard Bits |  | Read-Only
0x001B | Relay output status 3 | Standard Bits |  | Read-Only
0x001C | Relay output status 4 | Standard Bits |  | Read-Only
0x001D | Switch Port State 1 | Standard Bits |  | Read-Only
0x001E | Switch Port State 2 | Standard Bits |  | Read-Only
0x001F | Switch Port State 3 | Standard Bits |  | Read-Only
0x0020 | Switch Port State 4 | Standard Bits |  | Read-Only
0x0021 | (Reserved) | Actual Value |  | Read-Only
0x0022 | (Reserved) | Actual Value |  | Read-Only
0x0023 | (Reserved) | Actual Value |  | Read-Only
0x0024 | Current unit tooling No. | Actual Value |  | Read-Only
0x0025 | (Reserved) | Actual Value |  | Read-Only
0x0026 | (Reserved) | Actual Value |  | Read-Only
0x0027 | Compressor 1 target frequency | Actual Value |  | Read-Only
0x0028 | Compressor 2 target frequency | Actual Value |  | Read-Only
0x003F | State Reserved

## 2_Realtime_Data (0x0040-00FF)
2. Real-time Data Registers (0x0040 – 0x00FF) Including: temperature, voltage, pressure, expansion valve opening degree and other data
Address (hex) | Parameter Name | Range / Format | Default | Access | Note
0x0040 | Compressor operating frequency | Measured Value |  | Read-Only | Hz
0x0041 | Fan operating frequency / rotational speed | Measured Value |  | Read-Only | Hz
0x0042 | Electronic expansion valve steps count | Measured Value |  | Read-Only | P
0x0043 | Number of EVI valve steps | Measured Value |  | Read-Only | P
0x0044 | AC Input Voltage | Measured Value |  | Read-Only | V
0x0045 | AC Input Current | Measured Value |  | Read-Only | Display = Measured/10 [A]
0x0046 | Compressor Phase Current | Measured Value |  | Read-Only | Display = Measured/10 [A]
0x0047 | Compressor IPM Temperature | Measured Value |  | Read-Only | °C
0x0048 | High pressure saturation temperature | Measured Value |  | Read-Only | °C
0x0049 | Low pressure saturation temperature | Measured Value |  | Read-Only | °C
0x004A | External ambient temperature T1 | Measured Value |  | Read-Only | °C (×10 encoded)
0x004B | External coil tube (fin) T2 | Measured Value |  | Read-Only | °C (×10 encoded)
0x004C | Internal coil tube (plate replacement) T3 | Measured Value |  | Read-Only | °C (×10 encoded)
0x004D | Return air temperature T4 | Measured Value |  | Read-Only | °C (×10 encoded)
0x004E | Exhaust temperature T5 | Measured Value |  | Read-Only | °C (×10 encoded)
0x004F | Return water temperature T6 | Measured Value |  | Read-Only | °C (×10 encoded)
0x0050 | Water outlet temperature T7 | Measured Value |  | Read-Only | °C (×10 encoded)
0x0051 | Economizer inlet tube T8 | Measured Value |  | Read-Only | °C (×10 encoded)
0x0052 | Economizer outlet tube T9 | Measured Value |  | Read-Only | °C (×10 encoded)
0x0053 | Current device tooling No. | Measured Value |  | Read-Only
0x0054 | Water tank temperature | Measured Value |  | Read-Only | °C (×10 encoded)
0x0055 | Fluorine outlet temperature of Plate Heat exchanger | Measured Value |  | Read-Only | °C
0x0056 | Drive manufacturer | Measured Value |  | Read-Only
0x0057 | Pump speed PWM | Measured Value |  | Read-Only | %
0x0058 | Water flow | Measured Value |  | Read-Only | L/min
0x0059 | User return water temperature | Measured Value |  | Read-Only | °C
0x005A | Device input voltage | Measured Value |  | Read-Only | V
0x005B | Device input current | Measured Value |  | Read-Only | A
0x005C | Device input power | Measured Value |  | Read-Only | kW
0x005D | Total unit electricity consumption | Measured Value |  | Read-Only | kWh
0x005E | System 2 Compressor running frequency | Measured Value |  | Read-Only | Hz
0x005F | System 2 Fan running frequency / speed | Measured Value |  | Read-Only | Hz
0x0060 | System 2 Electronic Expansion Valve Steps | Measured Value |  | Read-Only | P
0x0061 | System 2 EVI valve Steps | Measured Value |  | Read-Only | P
0x0062 | System 2 AC Input voltage | Measured Value |  | Read-Only | V
0x0063 | System 2 AC Input Current | Measured Value |  | Read-Only | Display = Measured/10 [A]
0x0064 | System 2 Compressor Phase Current | Measured Value |  | Read-Only | Display = Measured/10 [A]
0x0065 | System 2 Compressor IPM Temperature | Measured Value |  | Read-Only | °C
0x0066 | System 2 High pressure saturation temperature | Measured Value |  | Read-Only | °C
0x0067 | System 2 Low pressure saturation temperature | Measured Value |  | Read-Only | °C
0x0068 | System 2 Outer coil tube (fin) | Measured Value |  | Read-Only | °C
0x0069 | System 2 Inner coil tube (Plate Heat Exchanger) | Measured Value |  | Read-Only | °C
0x006A | System 2 Return air temperature | Measured Value |  | Read-Only | °C
0x006B | System 2 Exhaust Air Temperature | Measured Value |  | Read-Only | °C
0x006C | System 2 Economizer Inlet Temperature | Measured Value |  | Read-Only | °C
0x006D | System 2 Economizer Outlet temperature | Measured Value |  | Read-Only | °C
0x0072 | Auxiliary Heating source Hot Water Temperature | Measured Value |  | Read-Only | °C
0x0073 | Auxiliary Heating source Heating Temperature | Measured Value |  | Read-Only | °C
0x0074 | Buffer Tank (for heating) Temperature | Measured Value |  | Read-Only | °C
0x0075 | Main Outlet Water Temperature | Measured Value |  | Read-Only | °C
0x00F0 | Water inlet temperature | Measured Value |  | Read-Only | °C
0x00F1 | Water outlet temperature | Measured Value |  | Read-Only | °C
0x00F2 | External environment temperature | Measured Value |  | Read-Only | °C
0x00F4 | Water tank temperature | Measured Value |  | Read-Only | °C
0x00FA | Set upper limit of floor heating / heating temperature | Measured Value |  | Read-Only | °C
0x00FB | Set lower limit of floor heating / heating temperature | Measured Value |  | Read-Only | °C
0x00FC | Set upper limit of hot water temperature | Measured Value |  | Read-Only | °C
0x00FD | Set lower limit of hot water temperature | Measured Value |  | Read-Only | °C
0x00FE | Set upper limit of refrigerating temperature | Measured Value |  | Read-Only | °C
0x00FF | Set lower limit of refrigerating temperature | Measured Value |  | Read-Only | °C

## 3_System_Params_P (0x0100-02FF)
3. Unit System Parameters P (0x0100 – 0x02FF) ¦ Access: Read-Write
Address (hex) | Parameter Name | Range | Access | Note / Unit
0x0100 | T1 external ambient temperature sensor | 0~10 | RW | 0: Enable, 1: Disable
0x0101 | High pressure switch settings | 0~10 | RW | 0: Enable, 1: Disable
0x0102 | Low pressure switch settings | 0~10 | RW | 0: Enable, 1: Disable
0x0103 | Water flow switch settings | 0~10 | RW | 0: Enable, 1: Disable
0x0104 | Thermal overload protection switch settings | 0~10 | RW | 0: Enable, 1: Disable
0x0105 | Linkage switch settings | 0~10 | RW | 0: Enable, 1: Disable 2: Constant Temperature 3: Heating Constant Temperature
0x0106 | Fan motor type setting | 0~10 | RW | 0: Enable, 1: Disable
0x0107 | High Pressure Protection Lockout Setting | 0~10 | RW | 0: Enable, 1: Disable
0x0108 | Low Pressure Protection Lockout Setting | 0~10 | RW | 0: Enable, 1: Disable
0x0109 | Exhaust Protection Lockout Setting | 0~10 | RW | 0: Enable, 1: Disable
0x010A | Water flow switch protection lock setting | 0~10 | RW | 0: Enable, 1: Disable
0x010B | High Pressure protection value | 40~150 | RW | °C
0x010C | High Pressure frequency limit value | 40~150 | RW | °C
0x010D | Low Pressure protection value | -50~-10 | RW | °C
0x010E | Low Pressure frequency limit value | -50~-10 | RW | °C
0x010F | Exhaust temperature protection value | 100~130 | RW | °C
0x0110 | Exhaust temperature limit frequency | 90~120 | RW | °C
0x0111 | Refrigeration fan speed increase value | 0~60 | RW | °C
0x0112 | Cooling fan deceleration value | 0~60 | RW | °C
0x0113 | Heating fan deceleration value | 0~60 | RW | °C
0x0114 | Heating fan speed increase value | 0~60 | RW | °C
0x0115 | The unit prohibits starting low temperature value | -40~-10 | RW | °C
0x0116 | Electric heating start ambient temperature value | -15~40 | RW | °C
0x0117 | Temperature difference between inlet and outlet water exceeds threshold | 10~30 | RW | °C
0x0118 | Return water temperature compensation value | -10~10 | RW | °C
0x0119 | Outlet water temperature compensation value | -10~10 | RW | °C
0x011A | Air conditioner return difference | 0~10 | RW | °C
0x011B | Floor heating difference | 0~10 | RW | °C
0x011C | Pump control mode when device reaches target temp and shuts down | 0~10 | RW | 0: Run 1: Stop 2: Cooling Run 3: Air Conditioning Run 4: Floor Heating Run
0x011D | Antifreeze water pump running time (every 10 min) | 0~10 | RW | min
0x011E | Defrost mode selection | 0~10 | RW | 0: Intelligent 1: Timer 2: Fast 3: Dew Point
0x011F | Enter defrost accumulated running time threshold | 0~120 | RW | °C
0x0120 | Enter defrost coil temperature value | -30~0 | RW | °C
0x0121 | Enter defrost temperature difference 1 | 0~20 | RW | °C
0x0122 | Enter defrost temperature difference 2 | 0~20 | RW | °C
0x0123 | Max defrost time | 0~30 | RW | min
0x0124 | Exit defrost coil temperature | 0~30 | RW | °C
0x0125 | Device reaching target temperature and shutdown mode | 0~10 | RW | 0: Intelligent shutdown 1: Reaching temperature shutdown 2: Intelligent Cooling
0x0126 | Heating main valve initial opening constant | -999~999 | RW
0x0127 | Pressure sensor settings | 0~10 | RW | 0: Enable, 1: Disable
0x0128 | Cooling target superheat correction value | -5~10 | RW | °C
0x0129 | Heating high pressure protection and frequency limit correction value | -10~10 | RW | °C
0x012A | Heating target superheat correction value | -5~10 | RW | °C
0x012B | Medium Pressure Switch Settings | 0~10 | RW | 0: Disable, 1: Enable
0x012C | Water flow switch failure detection settings | 0~10 | RW | 0: Enable, 1: Disable
0x012D | Communication address code | 1~16 | RW
0x012E | Return difference of opening of liquid injection solenoid valve | 0~15 | RW | °C
0x012F | EVI target superheat constant | 0~12 | RW
0x0130 | Whether the tank temperature probe is enabled | 0~10 | RW | 0: Disable, 1: Enable
0x0131 | Hot water frequency operating percentage | 30~100 | RW | %
0x0132 | Cooling target frequency constant A, Y=9X/5+A | -100~100 | RW
0x0133 | Cooling minimum frequency limit | 15~60 | RW | Hz
0x0134 | Cooling target frequency upper limit | 40~120 | RW | Hz
0x0135 | Cooling target frequency lower limit | 15~120 | RW | Hz
0x0136 | Heating target frequency constant B, Y=B-X | -100~100 | RW
0x0137 | Heating target frequency upper limit | 50~120 | RW | Hz
0x0138 | Heating target frequency lower limit | 20~120 | RW | Hz
0x0139 | Heating minimum frequency 1 | 15~60 | RW | Hz
0x013A | Heating minimum frequency 2 | 15~60 | RW | Hz
0x013B | Heating minimum frequency 3 | 15~60 | RW | Hz
0x013C | Hot water target frequency constant B, Y=B-X | -100~100 | RW
0x013D | Hot water target frequency upper limit, Y=B-X | 50~120 | RW | Hz
0x013E | Hot water target frequency lower limit, Y=B-X | 15~120 | RW | Hz
0x013F | Hot water minimum frequency 1 | 15~60 | RW | Hz
0x0140 | Hot water minimum frequency 2 | 15~60 | RW | Hz
0x0141 | Hot water minimum frequency 3 | 15~60 | RW | Hz
0x0142 | DC fan initial frequency | 20~60 | RW | Hz
0x0143 | DC fan heating minimum frequency | 20~60 | RW | Hz
0x0144 | DC fan heating maximum frequency | 20~80 | RW | Hz
0x0145 | DC fan cooling minimum frequency | 20~60 | RW | Hz
0x0146 | DC fan cooling maximum frequency | 20~80 | RW | Hz
0x0147 | Turn on enthalpy control frequency | 20~80 | RW | Hz
0x0148 | Stop enthalpy increase frequency | 20~80 | RW | Hz
0x0149 | Refrigeration main valve initial opening 1 | 20~480 | RW | P
0x014A | Refrigeration main valve initial opening 2 | 20~480 | RW | P
0x014B | Refrigeration main valve initial opening 3 | 20~480 | RW | P
0x014C | Minimum opening of refrigeration main valve | 0~300 | RW | P
0x014D | Minimum opening of heating main valve | 0~300 | RW | P
0x014E | Main valve maximum opening | 100~500 | RW | P
0x014F | Main valve initial opening constant c | 20~300 | RW | P
0x0150 | Main valve initial opening coefficient a | -999~999 | RW
0x0151 | Main valve initial opening coefficient b | -999~999 | RW
0x0152 | Auxiliary valve maximum opening | 100~500 | RW | P
0x0153 | Auxiliary valve minimum opening | 50~300 | RW | P
0x0154 | Main Valve Regulation Period | 10~120 | RW | S
0x0155 | Auxiliary valve initial opening constant c | -200~900 | RW
0x0156 | Auxiliary valve initial opening coefficient a | -999~999 | RW
0x0157 | Auxiliary valve initial opening coefficient b | -999~999 | RW
0x0158 | Silent mode compressor frequency | 20~70 | RW | Hz
0x0159 | Quiet mode fan frequency | 20~60 | RW | Hz
0x015A | Ambient temperature to enter EVI | 0~45 | RW | °C
0x015B | Time to forbid entering into EVI | 0~30 | RW | min
0x015C | Temperature Difference to enter EVI | 0~60 | RW | °C
0x015D | Compressor continuous running time to enter EVI | 0~20 | RW | min
0x015E | Auxiliary valve adjustment cycle | 10~120 | RW | S
0x015F | Cascade water pump running mode | 0~10 | RW | 0: Shared 1: Independent
0x0160 | Hot water return difference | 0~10 | RW | °C
0x0161 | Water tank temperature automatic compensation | 0~10 | RW | 0: Enable, 1: Disable
0x0162 | Manual compensation value of water tank temperature | -10~10 | RW | °C
0x0163 | Pump speed control temperature difference | 2~10 | RW | °C
0x0164 | PWM water pump minimum speed | 20~80 | RW | %
0x0165 | Pump control mode | 0~10 | RW | 0: AC 1: DC
0x0166 | Four-way valve control mode | 0~10 | RW | 0: Cooling Power On 1: Heating Power On
0x0167 | Mode switching minimum runtime | 0~10 | RW | min
0x0168 | Operating frequency percentage when switching modes | 20~100 | RW | %
0x0169 | Cooling mode operating ambient temperature limit | 10~60 | RW | °C
0x016A | Heating mode operating ambient temperature limit | 10~60 | RW | °C
0x016B | Hot water mode operating ambient temperature limit | 10~60 | RW | °C
0x016C | Hot water setting temperature upper limit | 30~80 | RW | °C
0x016D | Hot water setting temperature lower limit | 10~30 | RW | °C
0x016E | Heating set temperature upper limit | 30~80 | RW | °C
0x016F | Heating set temperature lower limit | 15~30 | RW | °C
0x0170 | Cooling set temperature upper limit | 20~40 | RW | °C
0x0171 | Cooling set temperature lower limit | 5~20 | RW | °C
0x0172 | Selection of the number of compressors | 1~2 | RW
0x0173 | Model selection | 0~10 | RW | 0: Heating & Cooling 1: Heating & Cooling & DHW Others: reserved
0x0174 | Unit temperature control method | 0~10 | RW | 0: Return water 1: Water Outlet
0x0175 | Ambient temperature to enter Antifreeze Mode | 0~10 | RW | °C
0x0176 | Antifreeze Inlet and Outlet Water Temperature | 0~20 | RW | °C
0x0177 | Refrigerant type | 0~20 | RW | 1: R410A 2: R32 3: R290
0x0178 | Low temperature start limit | 0~10 | RW | 0: Enable, 1: Disable
0x0179 | Heating frequency shield 1 stage low value | 0~120 | RW | Hz
0x017A | Heating frequency shield 1 stage high value | 0~120 | RW | Hz
0x017B | Heating frequency shield 2-stage low value | 0~120 | RW | Hz
0x017C | Heating frequency shield 2-stage high value | 0~120 | RW | Hz
0x017D | Heating frequency shield 3-stage low value | 0~120 | RW | Hz
0x017E | Heating frequency shield 3-stage high value | 0~120 | RW | Hz
0x017F | Cooling frequency shield 1 stage low value | 0~120 | RW | Hz
0x0180 | Cooling frequency shield 1 stage high value | 0~120 | RW | Hz
0x0181 | Cooling frequency shield 2-stage low value | 0~120 | RW | Hz
0x0182 | Cooling frequency shield 2-stage high value | 0~120 | RW | Hz
0x0183 | Cooling frequency shield 3-stage low value | 0~120 | RW | Hz
0x0184 | Cooling frequency shield 3-stage high value | 0~120 | RW | Hz
0x0185 | Fan module | 0~10 | RW | 0: Integral Module 1: Individual Module
0x0186 | Water flow too low protection value | 0~100 | RW | L/min
0x0187 | Temperature difference to start Anti-condensation | 0~50 | RW | °C
0x0188 | Ambient temperature to open Throttle bypass valve | -20~50 | RW | °C
0x0189 | Throttle Bypass Valve Delay Compressor | 0~999 | RW | S
0x018A | Defrost compressor frequency | 40~120 | RW | Hz
0x018B | Air conditioning electric heating options | 0~10 | RW | 0: Enable 1: Disable 2: Gas
0x018C | Hot water electric heating options | 0~10 | RW | 0: Enable 1: Disable 2: Gas
0x018D | Dew point duration of defrost | 0~60 | RW | min
0x018E | Dew point constant of defrost | 0~60 | RW
0x018F | Water Temperature to enter Defrost mode | 0~60 | RW | °C
0x0190 | Ambient temperature to enter Defrost mode | -20~30 | RW | °C
0x0191 | Water outlet antifreeze protection value | -20~10 | RW | °C
0x0192 | Pump range setting value | 0~100 | RW | L/min
0x0193 | Cooling Anti-Freeze Mode | 0~10 | RW | 0: Low pressure 1: Temp 2: Low pressure + temp
0x0194 | Cooling Anti-Freeze Temperature Value | -30~10 | RW | °C
0x0195 | Water out of the high limit frequency value | 40~80 | RW | °C
0x0196 | Secondary heating pump selection | 0~10 | RW | 0: Power on 1: Turn on 2: When linkage switch is open 3: Temp control
0x0197 | Hot water heat source return difference | 0~40 | RW | °C
0x0198 | Heating heat source return difference | 0~40 | RW | °C
0x0199 | Combined hot water heat source upper temperature limit | 15~80 | RW | °C
0x019A | Combined heating heat source upper temperature limit | 15~80 | RW | °C
0x019B | Compressor code (Function Reserved) | 0~9999 | RW
0x019C | Auxiliary electronic expansion valve selection | 0~10 | RW | 0: Enable, 1: Disable
0x019D | Auxiliary EEV – temperature difference to reduce | 0~99 | RW | °C
0x019E | Heating limit water temperature, start ambient temperature | -45~30 | RW | °C
0x019F | Limit temperature constant P159 | 0~150 | RW
0x01A0 | Limit temperature coefficient P160 | -500~500 | RW
0x01A1 | Auxiliary pump selection | 0~10 | RW | 0: Hot water 1: Cooling 2: Floor heating 3: Cooling and floor heating 4: All mode
0x01A2 | Anti-freezing interval for hot water pipes | 0~360 | RW | min
0x01A3 | Minimum feedback of pump speed regulation | 0~70 | RW | %
0x01A4 | Level control | 0~10 | RW | 0: Enable 1: Only Hot water 2: Only Heating 3: Disable
0x01A5 | Load return difference | 1~15 | RW | °C
0x01A6 | Load shedding hysteresis | 1~15 | RW | °C
0x01A7 | Emergency stop return difference | 1~15 | RW | °C
0x01A8 | Hot water mode start ratio | 1~100 | RW | %
0x01A9 | Non-hot water mode start ratio | 1~100 | RW | %
0x01AA | Loading cycle | 3~60 | RW | min
0x01AB | Shield low voltage switch ambient temperature | -50~0 | RW | °C
0x01AC | Target frequency constant c of DC fan | 40~70 | RW | Hz
0x01AD | Target frequency of heating fan lower limit | 20~65 | RW | Hz
0x01AE | Defrost valve opening | 0~480 | RW | P
0x01AF | Constant temperature operation cycle | 0~360 | RW | min
0x01B0 | Minimum defrosting time | 0~999 | RW | S
0x01B1 | Defrost segmented water temperature setting value | 0~80 | RW | °C
0x01B2 | High water temperature defrosting frequency | 40~120 | RW | Hz
0x01B3 | Strong mode frequency increase value | 0~40 | RW | Hz
0x01B4 | Powerful mode frequency cap increase value | 0~40 | RW | Hz
0x01B5 | Defrost mode | 0~2 | RW | 0: Current 1: Heating 2: Hot Water
0x01B6 | Pipe electric heating option | 0~2 | RW | 0: Full electricity 1: 3 kW 2: 6 kW 3: Disable
0x01B7 | Parameter password setting | 0~9999 | RW | 0: disable
0x01B8 | 35D working condition compressor frequency | 0~120 | RW | Hz
0x01B9 | 35C working condition compressor frequency | 0~120 | RW | Hz
0x01BA | 35B working condition compressor frequency | 0~120 | RW | Hz
0x01BB | 35A working condition compressor frequency | 0~120 | RW | Hz
0x01BC | 35E working condition compressor frequency | 0~120 | RW | Hz
0x01BD | 55D working condition compressor frequency | 0~120 | RW | Hz
0x01BE | 55C working condition compressor frequency | 0~120 | RW | Hz
0x01BF | 55B working condition compressor frequency | 0~120 | RW | Hz
0x01C0 | 55A working condition compressor frequency | 0~120 | RW | Hz
0x01C1 | 55E working condition compressor frequency | 0~120 | RW | Hz
0x01C2 | 35D working condition fan frequency | 0~60 | RW | Hz
0x01C3 | 35C working condition fan frequency | 0~60 | RW | Hz
0x01C4 | 35B working condition fan frequency | 0~60 | RW | Hz
0x01C5 | 35A working condition fan frequency | 0~60 | RW | Hz
0x01C6 | 35E working condition fan frequency | 0~60 | RW | Hz
0x01C7 | 55D working condition fan frequency | 0~60 | RW | Hz
0x01C8 | 55C working condition fan frequency | 0~60 | RW | Hz
0x01C9 | 55B working condition fan frequency | 0~60 | RW | Hz
0x01CA | 55A working condition fan frequency | 0~60 | RW | Hz
0x01CB | 55E working condition fan frequency | 0~60 | RW | Hz
0x01CC | 35D operating condition main valve target superheat | -10~10 | RW | °C
0x01CD | 35C working condition main valve target superheat | -10~10 | RW | °C
0x01CE | 35B working condition main valve target superheat | -10~10 | RW | °C
0x01CF | 35A working condition main valve target superheat | -10~10 | RW | °C
0x01D0 | 35E working condition main valve target superheat | -10~10 | RW | °C
0x01D1 | 55D operating condition main valve target superheat | -10~10 | RW | °C
0x01D2 | 55C operating condition main valve target superheat | -10~10 | RW | °C
0x01D3 | 55B working condition main valve target superheat | -10~10 | RW | °C
0x01D4 | 55A working condition main valve target superheat | -10~10 | RW | °C
0x01D5 | 55E working condition main valve target superheat | -10~10 | RW | °C
0x01D6 | Initial opening of main valve in 35D working condition | 0~500 | RW | P
0x01D7 | Initial opening of main valve in 35C working condition | 0~500 | RW | P
0x01D8 | Initial opening of main valve in 35B working condition | 0~500 | RW | P
0x01D9 | Initial opening of main valve in 35A working condition | 0~500 | RW | P
0x01DA | Initial opening of main valve in 35E working condition | 0~500 | RW | P
0x01DB | Initial opening of main valve in 55D working condition | 0~500 | RW | P
0x01DC | Initial opening of main valve in 55C working condition | 0~500 | RW | P
0x01DD | Initial opening of main valve in 55B working condition | 0~500 | RW | P
0x01DE | Initial opening of main valve in 55A working condition | 0~500 | RW | P
0x01DF | Initial opening of main valve in 55E working condition | 0~500 | RW | P
0x01E0 | 35D operating condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E1 | 35C operating condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E2 | 35B operating condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E3 | 35A working condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E4 | 35E working condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E5 | 55D working condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E6 | 55C working condition auxiliary valve target superheat | -10~10 | RW | °C
0x01E7 | 55B auxiliary valve target superheat | -10~10 | RW | °C
0x01E8 | 55A auxiliary valve target superheat | -10~10 | RW | °C
0x01E9 | 55E auxiliary valve target superheat | -10~10 | RW | °C
0x01EA | Initial opening of auxiliary valve in 35D working condition | 0~500 | RW | P
0x01EB | Initial opening of auxiliary valve in 35C working condition | 0~500 | RW | P
0x01EC | Initial opening of auxiliary valve in 35B working condition | 0~500 | RW | P
0x01ED | Initial opening of auxiliary valve in 35A working condition | 0~500 | RW | P
0x01EE | Initial opening of auxiliary valve in 35E working condition | 0~500 | RW | P
0x01EF | Initial opening of auxiliary valve in 55D working condition | 0~500 | RW | P
0x01F0 | Initial opening of auxiliary valve in 55C working condition | 0~500 | RW | P
0x01F1 | Initial opening of auxiliary valve in 55B working condition | 0~500 | RW | P
0x01F2 | Initial opening of auxiliary valve in 55A working condition | 0~500 | RW | P
0x01F3 | Initial opening of auxiliary valve in 55E working condition | 0~500 | RW | P
0x01F4 | Target water flow in 35 low water temperature condition | 0~100 | RW | L/min
0x01F5 | Target water flow under 55 high water temperature conditions | 0~100 | RW | L/min
0x01F6 | 35 Low water temperature rated fan frequency | 0~60 | RW | Hz
0x01F7 | Initial opening of main valve under 35 low water temperature rated condition | 0~500 | RW | P
0x01F8 | Initial opening of main valve under 55 high water temperature rated condition (fan freq) | 0~60 | RW | Hz
0x01F9 | Initial opening of main valve under 55 high water temperature rated condition | 0~500 | RW | P
0x01FA | Target superheat of main valve under 35 low water temperature rated condition | -10~10 | RW | °C
0x01FB | PFC shutdown current | 0~50 | RW | A
0x01FC | Target superheat of main valve under 55 high water temperature rated condition | -10~10 | RW | °C
0x01FD | PFC turn-on current | 0~50 | RW | A
0x01FE | Heating medium | 0~1 | RW | 0: Water 1: Antifreeze
0x01FF | Smart Grid Options | 0~1 | RW | 0: Enable 1: Disable
0x0200 | Peak grid running time | 30~999 | RW | min
0x0201 | Dual temperature zone selection | 0~2 | RW | 0: Auto 1: Manual 2: Disable
0x0202 | Mixed water regulating valve cycle | 5~20 | RW | min
0x0203 | Mixing valve full cycle time | 0~180 | RW | S
0x0204 | Max rotate speed of DC Water Pump | 50~99 | RW | %
0x0205 | Rotate speed of DC water pump under constant temperature | 20~99 | RW | %
0x0206 | Floor heating test mode selection | 0~1 | RW | 0: Enable 1: Disable

## 4_User_Params (0x0300-032F)
4. User Parameters (0x0300 – 0x032F) ¦ Access: Read-Write
Address (hex) | Parameter Name | Range | Default | Access | Note
0x0300 | Cooling set temperature |  | 12°C | Read-Write | °C
0x0301 | Heating set temperature |  | 55°C | Read-Write | °C
0x0302 | Hot water set temperature |  | 55°C | Read-Write | °C
0x0303 | Floor heating set temperature |  | 50°C | Read-Write | °C
0x0304 | Set mode | 0~7 |  | Read-Write | 0: Cooling 1: Heating 2: Hot water 3: Floor heating 4: Hot water + cooling 5: Hot water + heating 6: Reserve 7: Hot water + floor heating
0x0305 | On/Off | 0~1 |  | Read-Write | 0: Power off 1: Power on
0x0306 | Indoor temperature set point |  |  | Read-Write | °C
0x0307 | Frequency conversion mode | 0~2 |  | Read-Write | 0: Standard mode 1: High power mode 2: Silent mode
0x0308 | reserved |  |  | Read-Write
0x0309 | reserved |  |  | Read-Write
0x030A | Functional mode reserved |  |  | Read-Write
0x030B | (reserved) |  |  | Read-Write
0x030C | Heating/floor heating curve setting |  |  | Read-Write | Bit7-0: Heating Bit15-8: Floor Heating
0x030D | Hot water/cooling curve settings |  |  | Read-Write | Bit7-0: Hot Water Bit15-8: Refrigeration
0x030E | reserved parameters |  |  | Read-Write
0x030F | reserved parameters |  |  | Read-Write
0x0310 | reserved parameters |  |  | Read-Write
0x0311 | reserved parameters |  |  | Read-Write
0x0312 | reserved parameters |  |  | Read-Write
0x0313 | Cooling curve setting | 0-8, 11-18 | 0 | Read-Write | Protocol ≥ 130 valid
0x0314 | Heating curve setting | 0-8, 11-18 | 0 | Read-Write | Protocol ≥ 130 valid
0x0315 | Hot water curve setting | 0~4 | 0 | Read-Write | Protocol ≥ 130 valid
0x0316 | Floor heating curve setting | 0-8, 11-18 | 0 | Read-Write | Protocol ≥ 130 valid

## 5_User_Orders (0x0330-035F)
5. User Orders (0x0330 – 0x035F) ¦ Forced control of unit, frequency/speed
Address (hex) | Parameter Name | Bit / Range | Function | Access | Note
0x0330 | Crew control | Bit2 | Fast heat mode | Read-Write
0x0330 |  | Bit3 | Force into defrost | Read-Write
0x0330 |  | Bit4 | System Emptying mode | Read-Write
0x0330 |  | Bit5 | Refrigerant recovery | Read-Write
0x0330 |  | Bit8 | Forced to sterilizing | Read-Write
0x0330 |  | Bit10 | Allow backwater | Read-Write
0x0330 |  | Bit13 | Restore factory defaults | Read-Write
0x0331 | Load forced control | Bit0 | Compressor forced control | Read-Write
0x0331 |  | Bit1 | EEV forced control | Read-Write
0x0331 |  | Bit2 | EVI forced control | Read-Write
0x0331 |  | Bit3 | Fan motor forced control | Read-Write
0x0332 | Compressor 1 forced frequency | 0~120 | Hz | Read-Write
0x0333 | Compressor 2 forced frequency | 0~120 | Hz | Read-Write
0x0336 | EEV1 forced opening | 0~500 | P | Read-Write
0x0337 | EEV2 forced opening | 0~500 | P | Read-Write
0x033A | EVI1 forced opening | 0~500 | P | Read-Write
0x033B | EVI2 forced opening | 0~500 | P | Read-Write
0x033E | Fan motor forced speed | 0~80 | Hz | Read-Write
0x0343 | DC water pump control | 0~1 | 0: auto 1: manual | Read-Write
0x0344 | DC water pump output | 0~100 | % | Read-Write
0x0345 | PFC control | 0~2 | 0: auto 1: off 2: on | Read-Write

## 6_Version_Info (0x0360-036F)
6. Version Information (0x0360 – 0x036F) ¦ Product model, custom version, software version
Address (hex) | Parameter Name | Range | Access | Note
0x0360 | Program Version | 100 | Read-Only | V1.0
0x0361 | Product type | 0 | Read-Only | 0: Inverter commercial 1: Fixed frequency domestic 2: Fixed frequency commercial
0x0362 | Product type identification number | 1 | Read-Only | 0: Commercial inverter dual supply 1: Commercial inverter triple supply
0x0363 | Protocol version | / | Read-Only | V1.0.0
0x0364 | Temperature unit |  | Read-Only | °C / °F

## 7_System_Params_L (0x0800-083F)
7. Unit System Parameter L (0x0800 – 0x083F) ¦ L0-L10 remains unchanged; starts at L11
Address (hex) | Parameter Name | Range | Access | Note
0x0800 | Pipe electricity heating loading time | 1~300 | RW | min
0x0801 | High temperature sterilization function | 0~2 | RW
0x0802 | Sterilization interval days | 5~30 | RW | Day
0x0803 | Sterilization start time | 00:00~24:00 | RW
0x0804 | Sterilization run time | 0~50 | RW | min
0x0805 | Sterilization temperature setting | 50~80 | RW | °C
0x0806 | (Reserved) |  | RW
0x0807 | (Reserved) |  | RW
0x0808 | (Reserved) |  | RW
0x0809 | (Reserved) |  | RW
0x080A | (Reserved) |  | RW
0x080B | Return water mode | 0~10 | RW | 0: Disabled 1: Continuous water return 2: Cycle water return 3: Temperature difference water return
0x080C | Return water set temperature | 20~65 | RW | °C
0x080D | Return water temperature return difference | 1~15 | RW | °C
0x080E | Return water cycle | 3~90 | RW | min
0x080F | Return water time | 1~30 | RW | min

## 8_Coils (0x1000-10FF)
8. Bit Operation Instructions / Coils (0x1000 – 0x10FF) ¦ Access commands: 01H, 05H
Address (hex) | Parameter Name | Access | Note
0x1000 | High power mode | RW
0x1001 | Silent mode | RW
0x1002 | Reserved parameter | RW
0x1003 | Reserved parameter | RW
0x1004 | Reserved parameter | RW
0x1005 | Reserved parameter | RW
0x1006 | Reserved parameter | RW
0x1007 | Reserved parameter | RW
0x1008 | Reserved parameter | RW
0x1009 | Reserved parameter | RW
0x100A | Reserved parameter | RW
0x100B | Reserved parameter | RW
0x100C | Reserved parameter | RW
0x100D | Reserved parameter | RW
0x100E | Reserved parameter | RW
0x100F | Reserved parameter | RW
0x1010 | Reserved parameter | RW
0x1011 | Reserved parameter | RW
0x1012 | Fast heating mode | RW
0x1013 | Forced into defrost | RW
0x1014 | System emptying mode | RW
0x1015 | Refrigerant recovery | RW
0x1016 | Reserved parameter | RW
0x1017 | Reserved parameter | RW
0x1018 | Forced into sterilizing | RW
0x1019 | Reserved parameter | RW
0x101A | Allow water back | RW
0x101B | Reserved parameter | RW
0x101C | Reserved parameter | RW
0x101D | Restore factory defaults | RW
0x101E | Reserved parameter | RW
0x101F | Reserved parameter | RW
0x1020 | Compressor forced to control | RW
0x1021 | EEV forced to control | RW
0x1022 | EVI forced to control | RW
0x1023 | Fan motor forced to control | RW

## 9_Bit_Definitions
Bit Definitions for Status, Fault, Relay and Switch Registers
0x0000 – Running Status 1 (1=Function ON, 0=Function OFF)
Register | Bit | State / Description
0x0000 | Bit0 | Refrigerator recycling
| Bit1 | First level anti-freezing
| Bit2 | Second level anti-freezing
| Bit3 | Failure warning
| Bit4 | System 1 return oil
Bit5
Bit6
Bit7
| Bit8 | System defrost
Bit9
Bit10
Bit11
| Bit12 | Constant temperature shutdown
| Bit13 | Fault shutdown protection
| Bit14 | Machine run
| Bit15 | Machine wait to run
0x0001 – Running Status 2 (1=Function ON, 0=Function OFF)
Register | Bit | State / Description
0x0001 | Bit0 | High temperature Sterilization
| Bit1 | High temperature Sterilization Heat Preservation
Bit2
Bit3
Bit4
Bit5
Bit6
Bit7
Bit8
Bit9
| Bit10 | Controller on / off
Bit11
Bit12
Bit13
Bit14
Bit15
0x0002 – Fault State 1
Register | Bit | State / Description
0x0002 | Bit0 | Wrong phase fault
| Bit1 | Lack of phase fault
| Bit2 | Water flow fault
| Bit3 | Communication fault
| Bit4 | Emergency fault
| Bit5 | Use time expired
| Bit6 | Water tank (down) temperature fault
| Bit7 | Water inlet temperature fault
| Bit8 | Indoor temperature fault
| Bit9 | Environmental temperature fault
| Bit10 | User backwater temperature fault
| Bit11 | Cooling outlet water level is too low
| Bit12 | Water level switch fault
| Bit13 | Water outlet temperature fault
| Bit14 | Heating outlet water level is too high
| Bit15 | Protection against excessive water temperature difference between inlet and outlet
0x0003 – Fault State 2
Register | Bit | State / Description
0x0003 | Bit0 | Environmental low temperature protection
Bit1
Bit2
Bit3
Bit4
Bit5
| Bit6 | Indoor environment humidity fault
Bit7
Bit8
Bit9
Bit10
| Bit11 | Phase order dial error
Bit12
| Bit13 | Water pump 1 feedback fault
| Bit14 | Water pump 2 feedback fault
| Bit15 | Low water flow protection
0x0004 – Fault State 3
Register | Bit | State / Description
0x0004 | Bit0 | Phase sequence disconnected
| Bit1 | Expansion board communication
| Bit2 | Plate Heat Exchanger temperature fault
| Bit3 | Fan motor 1 communication fault
| Bit4 | Fan motor 2 communication fault
| Bit5 | Online model not matching error
| Bit6 | Auxiliary Heating Source Hot Water Sensor Error
| Bit7 | Auxiliary Heating Source Heating Sensor Error
| Bit8 | Buffer Tank Error
| Bit9 | Main Water Outlet Temperature Error
| Bit10 | Reserved
| Bit11 | Reserved
| Bit12 | Reserved
| Bit13 | Reserved
| Bit14 | Reserved
| Bit15 | Reserved
0x0005 – System 1 Fault State 1
Register | Bit | State / Description
0x0005 | Bit0 | High pressure switch protection
| Bit1 | Low pressure switch protection
| Bit2 | High pressure over high protection
| Bit3 | Low pressure over low protection
| Bit4 | Exhaust over protection
| Bit5 | Current protection
| Bit6 | Coil Temperature over protection
| Bit7 | Coil temperature fault
| Bit8 | Return air temperature fault
| Bit9 | Exhaust temperature fault
| Bit10 | Economizer Inlet temperature fault
| Bit11 | Economizer Outlet temperature fault
| Bit12 | Fan drive communication fault
| Bit13 | DC fan fault
| Bit14 | Refrigeration coil temperature fault
| Bit15 | Reserved
0x0006 – System 1 Fault State 2
Register | Bit | State / Description
0x0006 | Bit0 | High pressure sensor fault
| Bit1 | Low pressure sensor fault
| Bit2 | Middle Pressure switch fault
| Bit3 | Coil Temperature over high
| Bit4 | Compressor Drive Board communication fault
Bit5
Bit6
Bit7
Bit8
Bit9
Bit10
Bit11
Bit12
Bit13
Bit14
Bit15
0x0007 – System 1 Drive Fault State 1
Register | Bit | State / Description
0x0007 | Bit0 | IPM overcurrent / IPM module protection
| Bit1 | Compressor drive fault
| Bit2 | Compressor overcurrent
| Bit3 | Input voltage phase loss
| Bit4 | IPM current sampling fault
| Bit5 | Overheating shutdown of power components
| Bit6 | Precharge failed
| Bit7 | DC bus overvoltage
| Bit8 | DC bus undervoltage
| Bit9 | AC input undervoltage
| Bit10 | AC input overcurrent
| Bit11 | Input voltage sampling fault
| Bit12 | DSP and PFC communication fault
| Bit13 | Radiator temperature sensor fault
| Bit14 | Communication failure between DSP and communication board
| Bit15 | Abnormal communication with the main control board
0x0008 – System 1 Drive Fault State 2
Register | Bit | State / Description
0x0008 | Bit0 | Compressor overcurrent alarm
| Bit1 | Compressor field weakening protection alarm
| Bit2 | PIM overheat alarm
| Bit3 | PFC overheat alarm
| Bit4 | AC input overcurrent alarm
| Bit5 | EEPROM fault alarm
| Bit6 | NA
| Bit7 | EEPROM refresh completed
| Bit8 | Temperature sensing fault frequency limit
| Bit9 | AC undervoltage and frequency limit protection alarm
| Bit10 | NA
| Bit11 | NA
| Bit12 | NA
| Bit13 | NA
| Bit14 | NA
| Bit15 | NA
0x0009 – System 1 Drive Fault State 3
Register | Bit | State / Description
0x0009 | Bit0 | IPM module thermal shutdown
| Bit1 | Compressor phase loss
| Bit2 | Compressor overload
| Bit3 | Input current sampling fault
| Bit4 | PIM supply voltage fault
| Bit5 | Precharge circuit voltage fault
| Bit6 | EEPROM fault
| Bit7 | AC input overvoltage fault
| Bit8 | Microelectronics fault
| Bit9 | Compressor model code fault
| Bit10 | Current sampling signal overcurrent
| Bit11 | NA
| Bit12 | NA
| Bit13 | NA
| Bit14 | NA
| Bit15 | NA
0x0019 – Electric Relay State 1
Register | Bit | State / Description
0x0019 | Bit0 | Hot water electric heating
| Bit1 | Fan high wind
Bit2
| Bit3 | Fan low wind
| Bit4 | Air conditioner electric heating
| Bit5 | Floor heating electric heating
| Bit6 | Main engine circulating water pump
Bit7
Bit8
| Bit9 | Electric crankshaft heating
| Bit10 | Chassis electric heating
| Bit11 | Return valve / pump
Bit12
Bit13
| Bit14 | Air conditioner solenoid valve / three-way valve
| Bit15 | Floor heating solenoid valve / three-way valve
0x001A – Electric Relay State 2
Register | Bit | State / Description
0x001A | Bit0 | Compressor 1
| Bit1 | Liquid injection solenoid valve 1
| Bit2 | Enthalpy solenoid valve 1
| Bit3 | Four-way valve 1
| Bit4 | Throttle bypass valve 1
| Bit5 | Fan motor 1
Bit6
Bit7
| Bit8 | Auxiliary Heating Pump
Bit9
| Bit10 | Compressor 2
| Bit11 | Spray solenoid valve 2
| Bit12 | Enthalpy increasing solenoid valve 2
| Bit13 | 4-Way 2
Bit14
Bit15
0x001B – Electric Relay State 3
Register | Bit | State / Description
0x001B | Bit0
Bit1
Bit2
Bit3
Bit4
Bit5
| Bit6 | Expansion Tank Heating Element
| Bit7 | Auxiliary Heat Source Hot water Pump
| Bit8 | Auxiliary Heat Source Heating Pump
| Bit9 | Gas Output
Bit10
Bit11
Bit12
Bit13
Bit14
Bit15
0x001C – Electric Relay State 4
Register | Bit | State / Description
0x001C | Bit0 | Pipeline electric heating 1
| Bit1 | Pipeline electric heating 2
Bit2
Bit3
Bit4
Bit5
Bit6
Bit7
Bit8
Bit9
Bit10
Bit11
Bit12
Bit13
Bit14
Bit15
0x001D – Switch Port State 1
Register | Bit | State / Description
0x001D | Bit0 | SW1
| Bit1 | SW2
| Bit2 | SW3
| Bit3 | SW4
| Bit4 | SW5
| Bit5 | SW6
| Bit6 | SW7
| Bit7 | SW8
| Bit8 | Water Flow Switch
Bit9
| Bit10 | House Heating Linkage Switch
| Bit11 | Auxiliary Hot Water Linkage Switch
| Bit12 | Linkage switch
| Bit13 | Emergency switch
Bit14
Bit15
0x001E – Switch Port State 2
Register | Bit | State / Description
0x001E | Bit0
Bit1
Bit2
Bit3
Bit4
Bit5
Bit6
| Bit7 | High Pressure 1 Switch
| Bit8 | Low Pressure 1 switch
| Bit9 | Medium Pressure 1 switch
| Bit10 | High Pressure 2 Switch
| Bit11 | Low Pressure 2 switch
| Bit12 | Medium Pressure 2 switch
Bit13
Bit14
Bit15
0x001F – Switch Port State 3
Register | Bit | State / Description
0x001F | Bit0
Bit1
Bit2
Bit3
Bit4
| Bit5 | Auxiliary Heating Linkage Switch
Bit6
Bit7
Bit8
Bit9
Bit10
Bit11
Bit12
Bit13
Bit14
Bit15